COMPREHENSIVE P&ID RECONSTRUCTION DOCUMENT

Fuel Gas Knockout Drum System (PP01-362-V001)

Complete Technical Specification with All Connections

SECTION 1: MAIN EQUIPMENT SPECIFICATIONS

1.1 Fuel Gas Knockout Drum (PP01-362-V001)

The central process vessel is a horizontal knockout drum designed to remove entrained liquids from fuel gas streams originating from the DS1 and DS3 scrapper receivers. The vessel separates liquid droplets from the gas phase through gravity settling and velocity reduction before the gas proceeds to the Fuel Gas Treatment Package.

1.1.1 Equipment Identification

| Parameter | Value |
| --- | --- |
| Equipment Tag | PP01-362-V001 |
| Operating Tag | 362-V001 |
| Service | Fuel Gas Knockout Drum |
| Vessel Type | Horizontal Cylindrical Drum |

1.1.2 Dimensional Data

| Parameter | Value |
| --- | --- |
| Internal Diameter (ID) | 2200 mm |
| Length (Tangent to Tangent) | 5500 mm |
| Orientation | Horizontal |

1.1.3 Design Conditions

| Parameter | Value |
| --- | --- |
| Design Pressure | 14 barg |
| Design Temperature | -20°C to 100°C (NOTE-7) |
| Operating Pressure | 9.0 to 10.4 barg |
| Operating Temperature | 23°C to 72°C |

1.1.4 Material and Construction

| Parameter | Value |
| --- | --- |
| Shell Material | Carbon Steel (CS) |
| Corrosion Allowance | 3 mm |
| Internal Coating | Epoxy Ceramic Coating |
| External Insulation | None |
| Trim Number | PP01-362-V001-TX0001-B03F9 |

1.1.5 Vessel Internals

The vessel contains a mist eliminator designated as MW 24" (24-inch Mist Wire mesh demister pad). This wire mesh pad is positioned in the gas flow path upstream of the gas outlet nozzle N2. The demister captures entrained liquid droplets from the gas stream before the gas exits the vessel, improving separation efficiency.

1.1.6 Level Settings

| Level Designation | Height from Vessel Bottom | Function |
| --- | --- | --- |
| HHLL (High-High Liquid Level) | 1300 mm | Alarm and Trip |
| HLL (High Liquid Level) | 1150 mm | Alarm |
| NLL (Normal Liquid Level) | 800 mm | Normal Operating Level |
| LLL (Low Liquid Level) | 450 mm | Alarm |
| LLLL (Low-Low Liquid Level) | 300 mm | Alarm and Trip |

SECTION 2: COMPLETE NOZZLE SCHEDULE AND CONNECTIONS

2.1 Nozzle N1: Pressure Safety Valve (PSV) Header Connection

Nozzle N1 is the primary pressure relief connection point, serving as the common inlet header for two parallel Pressure Safety Valves (PSV-001 and PSV-002) that protect the vessel from overpressure conditions.

2.1.1 Nozzle Specifications

| Parameter | Value |
| --- | --- |
| Nozzle Tag | N1 |
| Nozzle Size | 14 inch |
| Service | PSV Relief Header |
| Rating | 300# |
| Orientation | Top of vessel |

2.1.2 Main Header Line from Nozzle N1

The main relief header line originates at nozzle N1 with designation 14"-PP01-362-GF0001-B01E9-PP. This 14-inch line serves as the common supply header for both PSV branches.

From nozzle N1, the 14-inch main header runs horizontally. At the first junction point, a parallel branch line designated 14"-PP01-362-GF0004-B01E9-PP splits off to feed PSV-002, while the main header continues to PSV-001.

2.1.3 PSV-001 Flow Path (Complete Component Sequence)

Starting from the main header line 14"-PP01-362-GF0001-B01E9-PP:

- HV0004: 14-inch Ball Valve - Inlet isolation valve for PSV-001, maintained in Locked Open (LO) position during normal operation

- HV0005: 1-inch Drain Valve - Located between HV0004 and the inlet reducer, provides drainage capability for the inlet piping

- Reducer: Concentric reducer 14" × 8" - Reduces line size from 14 inches to 8 inches to match PSV inlet connection

- PSV-001: Pressure Safety Valve

  - Set Pressure: 14.0 barg

  - Relief Case: DS-3 PCV Failure

  - Orifice Size: 8T10

- Reducer: Concentric reducer 10" × 16" - Expands from PSV outlet to 16-inch flare header

- HV0038: 1-inch Drain Valve - Located between PSV outlet reducer and HV0039

- HV0039: 16-inch Ball Valve - Outlet isolation valve

Outlet Line: 16"-PP01-500-VK0066-B01B8 routes to HP Flare Header (Drawing N-PG-PP01-PR-PID-0021-001)

2.1.4 PSV-002 Flow Path (Complete Component Sequence)

Starting from the branch line 14"-PP01-362-GF0004-B01E9-PP:

- HV0006: 14-inch Ball Valve - Inlet isolation valve for PSV-002, maintained in Locked Open (LO) position during normal operation

- HV0007: 1-inch Drain Valve - Located between HV0006 and the inlet reducer

- Reducer: Concentric reducer 14" × 8" - Reduces line size from 14 inches to 8 inches

- PSV-002: Pressure Safety Valve

  - Set Pressure: 14.0 barg

  - Relief Case: DS-3 PCV Failure

  - Orifice Size: 8T10

- Reducer: Concentric reducer 10" × 16" - Expands from PSV outlet

- HV0041: 1-inch Drain Valve - Located between PSV outlet reducer and outlet ball valve

- HV0041: 16-inch Ball Valve - Outlet isolation valve (Note: Tag HV0041 appears duplicated for both drain and ball valve in source documentation - requires field verification)

Outlet Line: 16"-PP01-500-VK0008-B01B8 routes to HP Flare Header (Drawing N-PG-PP01-PR-PID-0021-001)

2.1.5 PSV Data Summary Table

| Parameter | PSV-001 | PSV-002 |
| --- | --- | --- |
| Tag | PSV-001 | PSV-002 |
| Set Pressure | 14.0 barg | 14.0 barg |
| Relief Case | DS-3 PCV Failure | DS-3 PCV Failure |
| Orifice Size | 8T10 | 8T10 |
| Inlet Size | 8" (via 14"×8" reducer) | 8" (via 14"×8" reducer) |
| Outlet Size | 10" (to 16" via reducer) | 10" (to 16" via reducer) |
| Inlet Isolation | HV0004 (14" Ball, LO) | HV0006 (14" Ball, LO) |
| Outlet Isolation | HV0039 (16" Ball) | HV0041 (16" Ball) |
| Inlet Drain | HV0005 (1") | HV0007 (1") |
| Outlet Drain | HV0038 (1") | HV0041 (1") |

2.2 Nozzle N2: Main Gas Outlet

Nozzle N2 is the primary gas outlet from the vessel, located at the top of the drum. Gas exits through this nozzle after passing through the internal mist eliminator (MW 24"). The outlet system splits into three distinct flow paths serving different functions.

2.2.1 Nozzle Specifications

| Parameter | Value |
| --- | --- |
| Nozzle Tag | N2 |
| Nozzle Size | 16 inch |
| Service | Main Gas Outlet |
| Rating | 300# |
| Orientation | Top of vessel |

2.2.2 Primary Outlet Header

From nozzle N2, the main gas outlet line is designated 16"-PP01-362-GF0002-B01E9-PP. Immediately at the nozzle, the following components are installed:

- Blind Flange: 16-inch blind flange for isolation capability

- PG-0001: Pressure Gauge - Local pressure indication

- HV0015: Isolation valve for pressure gauge connection

The 16-inch header then splits into three distinct paths:

2.2.3 Path 1: Fuel Gas Treatment Package (Main Process Flow)

The primary process flow continues as the 16-inch main line 16"-PP01-362-GF0002-B01E9-PP routing directly to the Fuel Gas Treatment Package.

Destination: Fuel Gas Treatment Package (Drawing N-PG-PP01-PR-PID-0009-001)

This is the normal operating flow path for treated fuel gas exiting the knockout drum.

2.2.4 Path 2: Blowdown/Depressurization to HP Flare

A 6-inch branch line provides blowdown and depressurization capability:

Line Designation: 6"-PP01-362-GF0009-B01E9-PP

Component sequence from the branch point:

- HV0061: 6-inch Ball Valve - Blowdown isolation valve

- BDV-0001: Control Valve (Blowdown Valve) - Automated blowdown control

- Reducer: 6" to 8" expander

- HV0029: 8-inch Ball Valve - Downstream isolation

Piping Specification Change: At the reducer/HV0029 location, the piping specification changes from B01E9 to B01B8.

Exit Line: 8"-PP01-500-VK0026-B01B8 routing to HP Flare Header (Drawing N-PG-PP01-PR-PID-0021-001)

2.2.5 Path 3: Pressure Control to HP Flare

An 8-inch branch line provides continuous pressure control capability:

Line Designation: 8"-PP01-362-GF0003-B01E9-PP

Main Control Path Component Sequence:

- HV0016: 8-inch Ball Valve - Upstream isolation

- HV0017: 1-inch Drain Valve - Located between HV0016 and PV-0002

- PV-0002: Pressure Control Valve (Globe type) - Main pressure control valve receiving signal from PIC-0002

- HV0020: 1-inch Drain Valve - Located downstream of PV-0002

- Reducer: 8" to 10" expander

- HV0021: 10-inch Ball Valve - Downstream isolation

Bypass Path (Parallel to PV-0002):

A 4-inch bypass line runs parallel to the main control valve for manual override or maintenance bypass:

- HV0018: 4-inch Ball Valve - Bypass inlet isolation

- HV0019: 4-inch Globe Valve - Bypass throttling/isolation

Piping Specification Change: At the HV0021 location, the piping specification changes from B01E9 to B01B8.

Exit Line: 10"-PP01-500-VK0010-B01B8 routing to HP Flare Header (Drawing N-PG-PP01-PR-PID-0021-001)

2.3 Nozzle N3: Condensate/Liquid Outlet

Nozzle N3 is located at the bottom of the vessel and serves as the primary liquid outlet for separated condensate. The liquid is routed to the Condensate Storage Vessel.

2.3.1 Nozzle Specifications

| Parameter | Value |
| --- | --- |
| Nozzle Tag | N3 |
| Nozzle Size | 4 inch |
| Service | Condensate Liquid Outlet |
| Rating | 300# |
| Orientation | Bottom of vessel |

2.3.2 Main Outlet Line Configuration

Line Designation: 4"-PP01-512-PK0005-C01N9-PP (originating at nozzle, specification starts as C01N9)

The line transitions to 4"-PP01-512-PK0006-B01M8-PP downstream.

Destination: Condensate Storage Vessel (Drawing N-PG-PP01-PR-PID-0024-001)

2.3.3 Main Flow Path Component Sequence

From nozzle N3, the main liquid control path includes:

- HV0065: 2-inch Gate Valve (Normally Closed) - Drain valve located immediately at the nozzle

- HV0027: 4-inch Gate Valve - Primary upstream isolation

- EZV-0001: Emergency Shutdown Valve - 4-inch automated isolation valve for emergency shutoff

- HV0028: 4-inch Gate Valve - Primary downstream isolation

2.3.4 Level Control Bypass Path

A bypass path exists parallel to the main EZV-0001 valve for level control during normal operation. This bypass branches off before EZV-0001 and rejoins after HV0028:

Bypass Entry Point: Junction with HV0032 (2-inch valve)

Bypass Component Sequence:

- HV0032: 2-inch Gate Valve - Bypass inlet isolation

- Reducer: 2" to 1.5" reducer

- HV0004: 1.5-inch Ball Valve (NOTE: This HV0004 is different from PSV inlet HV0004 - tag duplication in source)

- HV0029: 1.5-inch Valve

- LV-0001: Level Control Valve - 1.5-inch control valve receiving signal from LIC-0001

- HV0030: 1.5-inch Valve (with 0.5-inch drain HV0030 nearby - tag duplication noted)

- Reducer: 1.5" to 4" expander

- Rejoins main 4-inch line before final destination

2.3.5 Instrumentation Connection

A 2-inch blind flange branch connection from the outlet line provides instrumentation access:

- CIT-0001: Corrosion Indication Transmitter

- CI-0001: Corrosion Indicator

These instruments monitor corrosion in the liquid outlet piping.

2.3.6 Service Designation

The 4-inch outlet line is designated as TWO PHASE per NOTE-10, indicating it carries both liquid and some entrained gas.

2.4 Nozzle N4: Fuel Gas Inlet (From DS-3 Scrapper Receiver)

Nozzle N4 receives fuel gas from the DS-3 Scrapper Receiver system. This is one of two primary inlet connections to the knockout drum.

2.4.1 Nozzle Specifications

| Parameter | Value |
| --- | --- |
| Nozzle Tag | N4 |
| Nozzle Size | 12 inch |
| Service | Fuel Gas Inlet from DS-3 |
| Rating | 300# |
| Orientation | Top of vessel |

2.4.2 Inlet Line Configuration

Source Drawing: N-PG-PP01-PR-PID-0007-001 (DS-3 Scrapper Receiver)

Line Designation: 16"-PP01-361-GF0031-B03F9-PP

Special Requirement: NO POCKETS (NOTE-10) - The line must be self-draining with no low points where liquid can accumulate.

2.4.3 Component Sequence (From Source to Vessel)

Following the flow direction from the DS-3 Scrapper Receiver toward the vessel:

- Line Origin: 16-inch line exits Drawing N-PG-PP01-PR-PID-0007-001

- Check Valve: 16-inch Check Valve - Prevents backflow toward the scrapper receiver

- HV0203: 16-inch Ball Valve - Main inlet isolation valve

- Reducer: Concentric reducer 16" to 12" - Reduces line size to match nozzle N4

- Nozzle N4: 12-inch vessel nozzle connection

2.4.4 Connection Notes

- NOTE-2 applies to this nozzle connection specifying installation requirements

- The check valve and ball valve arrangement allows isolation of the inlet while preventing reverse flow during upset conditions

2.5 Nozzle N5: Fuel Gas Inlet (From DS-1 Scrapper Receiver)

Nozzle N5 receives fuel gas from the DS-1 Scrapper Receiver system. This is the second primary inlet connection to the knockout drum.

2.5.1 Nozzle Specifications

| Parameter | Value |
| --- | --- |
| Nozzle Tag | N5 |
| Nozzle Size | 12 inch |
| Service | Fuel Gas Inlet from DS-1 |
| Rating | 300# |
| Orientation | Top of vessel |

2.5.2 Inlet Line Configuration

Source Drawing: N-PG-PP01-PR-PID-0005-001 (DS-1 Scrapper Receiver)

Line Designation: 16"-PP01-361-GF0014-B03F9-PP

Special Requirement: NO POCKETS (NOTE-10) - The line must be self-draining.

2.5.3 Component Sequence (From Source to Vessel)

Following the flow direction from the DS-1 Scrapper Receiver toward the vessel:

- Line Origin: 16-inch line exits Drawing N-PG-PP01-PR-PID-0005-001

- Check Valve: 16-inch Check Valve - Prevents backflow toward the scrapper receiver

- HV0094: 16-inch Ball Valve - Main inlet isolation valve

- Reducer: Concentric reducer 16" to 12" - Reduces line size to match nozzle N5

- Nozzle N5: 12-inch vessel nozzle connection

2.5.4 Connection Notes

- NOTE-2 applies to this nozzle connection specifying installation requirements

- Configuration mirrors N4 inlet for operational consistency

2.6 Nozzle N6 (N6A & N6B): Level Transmitter Bridle (LZT-0002C)

Nozzles N6A and N6B form a bridle pair for level transmitter LZT-0002C. This is part of the upper interface level measurement system.

2.6.1 Nozzle Specifications

| Parameter | N6A | N6B |
| --- | --- | --- |
| Nozzle Size | 2 inch | 2 inch |
| Service | Level Bridle - Upper | Level Bridle - Lower |
| Rating | 300# | 300# |

2.6.2 Instrumentation

- LZT-0002C: Level Transmitter (Guided Wave Radar type)

- Part of 2oo3 voting logic for safety level measurement

2.6.3 Component Configuration

N6A Connection Path:

- Nozzle N6A (2")

- HV0034: 2-inch Solenoid Valve - Upper isolation

N6B Connection Path:

- Nozzle N6B (2")

- HV0035: 2-inch Solenoid Valve - Lower isolation

Common Instrumentation Line:

- Line Number: 1"-PP01-512-PK0081-B03F9-PP

- HV0044: 1-inch Gate Valve - Upstream of LZT-0002C

- 2-inch Blind Flange: Located before HV0044 for instrument access

- HV0045: 1-inch Gate Valve - Downstream isolation

2.6.4 Header Connection

This bridle connects to the Top Common Header line 1"-PP01-512-PK0079-B03F9-PP, joining before the common drain valve HV0056.

2.7 Nozzle N7 (N7A & N7B): Level Transmitter Bridle (LIT-0001)

Nozzles N7A and N7B form a bridle pair for level indicating transmitter LIT-0001. This provides primary level measurement for process control.

2.7.1 Nozzle Specifications

| Parameter | N7A | N7B |
| --- | --- | --- |
| Nozzle Size | 2 inch | 2 inch |
| Service | Level Bridle - Upper | Level Bridle - Lower |
| Rating | 300# | 300# |

2.7.2 Instrumentation

- LIT-0001: Level Indicating Transmitter - Primary level measurement for LIC-0001 controller

2.7.3 Component Configuration

N7A Connection Path:

- Nozzle N7A (2")

- HV0022: 2-inch Solenoid Valve - Upper isolation

- HV0028: 1-inch Drain Valve - Located upstream of HV0022

N7B Connection Path:

- Nozzle N7B (2")

- HV0023: 2-inch Solenoid Valve - Lower isolation

Common Instrumentation Line:

- Line Number: 1"-PP01-512-PK0077-B03F9-PP

- HV0029: 1-inch Gate Valve - After N7A connection junction

- HV0049: 1-inch Gate Valve

- HV0050: 1-inch Gate Valve - Further downstream

2.7.4 Header Connection

This bridle connects to the Bottom Common Header line 1"-PP01-512-PK0054-B01M8-PP, which correlates with the N3 liquid outlet piping system.

2.8 Nozzle N8: Service/Maintenance Connection

Nozzle N8 is a standalone service connection for maintenance, drainage, or utility access.

2.8.1 Nozzle Specifications

| Parameter | Value |
| --- | --- |
| Nozzle Tag | N8 |
| Nozzle Size | 3 inch |
| Service | Maintenance/Service |
| Rating | 300# |

2.8.2 Component Configuration

- HV0064: 3-inch Gate Valve - Direct connection to nozzle for isolation

No further downstream piping is detailed; the valve provides isolation for maintenance access to the vessel.

2.9 Nozzle N9: Manual Drain to UC (Utility Connection)

Nozzle N9 provides a manual drain connection from the vessel bottom to a utility containment structure (UC).

2.9.1 Nozzle Specifications

| Parameter | Value |
| --- | --- |
| Nozzle Tag | N9 |
| Nozzle Size | 2 inch |
| Service | Manual Drain |
| Rating | 300# |
| Orientation | Bottom of vessel |

2.9.2 Line Configuration

Line Designation: 2"-PP01-567-GF0002-B03F9

Destination: UC (Utility Connection - described as bucket/pit type containment structure)

2.9.3 Component Sequence (From Nozzle to UC)

- Nozzle N9 (2")

- HV0002: 2-inch Gate Valve - Primary isolation (Note: Source indicates Normally Closed position)

- HV0051: 1-inch Drain Valve - Located between HV0002 and check valve

- HV0001: 2-inch Check Valve - Prevents backflow from UC to vessel

- Reducer: 2" to 0.75" reducer

- UC: Utility Connection termination point

2.10 Nozzle N10 (N10A & N10B): Level Transmitter Bridle (LIT-0003)

Nozzles N10A and N10B form a bridle pair for level indicating transmitter LIT-0003.

2.10.1 Nozzle Specifications

| Parameter | N10A | N10B |
| --- | --- | --- |
| Nozzle Size | 2 inch | 2 inch |
| Service | Level Bridle - Upper | Level Bridle - Lower |
| Rating | 300# | 300# |

2.10.2 Instrumentation

- LIT-0003: Level Indicating Transmitter

2.10.3 Component Configuration

N10A Connection Path:

- Nozzle N10A (2")

- HV0030: 2-inch Solenoid Valve

- HV0003: 1-inch Drain Valve - Located before HV0030

N10B Connection Path:

- Nozzle N10B (2")

- HV0031: 2-inch Solenoid Valve

Common Instrumentation Line:

- Line Number: 1"-PP01-512-PK0078-B03F9-PP

- 2-inch Blind Flange: Located before LIT-0003 instrument

- HV0033: 1-inch Gate Valve - After N10B connection

- HV0051: 1-inch Gate Valve - Further downstream

2.10.4 Header Connection

Piping Specification Change: At a junction point, the specification changes from B03F9 to B01M8.

This bridle connects to the Bottom Common Header line 1"-PP01-512-PK0054-B01M8-PP, joining with N7 and N18 assemblies.

2.11 Nozzle N11 (N11A & N11B): Level Transmitter Bridle (LZT-0002B)

Nozzles N11A and N11B form a bridle pair for level transmitter LZT-0002B, part of the safety level measurement system.

2.11.1 Nozzle Specifications

| Parameter | N11A | N11B |
| --- | --- | --- |
| Nozzle Size | 2 inch | 2 inch |
| Service | Level Bridle - Upper | Level Bridle - Lower |
| Rating | 300# | 300# |

2.11.2 Instrumentation

- LZT-0002B: Level Transmitter (Guided Wave Radar type)

- Part of 2oo3 voting logic for safety level measurement

- Associated with LI-0002B (Level Indicator) and LV-0002B (Level Valve)

2.11.3 Component Configuration

N11A (also referred to as L11A) Connection Path:

- Nozzle N11A (2")

- HV0036: 2-inch Solenoid Valve

N11B (also referred to as L11B) Connection Path:

- Nozzle N11B (2")

- HV0037: 2-inch Solenoid Valve

Common Instrumentation Line:

- Line Number: 1"-PP01-512-PK0080-B03F9-PP

- HV0042: 1-inch Drain Valve - Between LZT instrument and N11A junction

- 2-inch Blind Flange: Located between line and LZT instrument

- HV0043: 1-inch Gate Valve - After N11B connection

2.11.4 Header Connection

This bridle connects to the Top Common Header line 1"-PP01-512-PK0079-B03F9-PP, joining before the common drain valve HV0056.

2.12 Nozzle N12 (N12A & N12B): Level Transmitter Bridle (LZT-0002A)

Nozzles N12A and N12B form a bridle pair for level transmitter LZT-0002A, part of the safety level measurement system.

2.12.1 Nozzle Specifications

| Parameter | N12A | N12B |
| --- | --- | --- |
| Nozzle Size | 2 inch | 2 inch |
| Service | Level Bridle - Upper | Level Bridle - Lower |
| Rating | 300# | 300# |

2.12.2 Instrumentation

- LZT-0002A: Level Transmitter (Guided Wave Radar type)

- Part of 2oo3 voting logic for safety level measurement

- Associated with LI-0002A (Level Indicator) and LV-0002A (Level Valve)

2.12.3 Component Configuration

N12A Connection Path:

- Nozzle N12A (2")

- HV0038: 2-inch Solenoid Valve

N12B Connection Path:

- Nozzle N12B (2")

- HV0039: 2-inch Solenoid Valve

Common Instrumentation Line:

- HV0040: 1-inch Drain Valve - At junction between N12A connection and LZT instrument

- 2-inch Blind Flange: Located before drain valve

- HV0041: 1-inch Gate Valve - On connection line between N12A and N12B

2.12.4 Header Connection

This bridle connects to the Top Common Header line 1"-PP01-512-PK0079-B03F9-PP, connecting near the 1-inch gate valve HV0052.

2.13 Nozzle N13: Pressure Transmitter Connection (PZT-0001A)

Nozzle N13 provides the first pressure measurement for the 2oo3 voting logic safety system.

2.13.1 Nozzle Specifications

| Parameter | Value |
| --- | --- |
| Nozzle Tag | N13 |
| Nozzle Size | 2 inch |
| Service | Pressure Instrumentation |
| Rating | 300# |
| Orientation | Top of vessel |

2.13.2 Component Configuration

- Nozzle N13 (2")

- HV0011: 2-inch Solenoid Valve - Isolation for transmitter

2.13.3 Instrumentation

- PZT-0001A: Pressure Transmitter - Provides input to 2oo3 voting logic (362-004)

- PI-0001A: Pressure Indicator - Local indication with HH (High-High) alarm

2.14 Nozzle N14: Pressure Transmitter Connection (PZT-0001B)

Nozzle N14 provides the second pressure measurement for the 2oo3 voting logic safety system.

2.14.1 Nozzle Specifications

| Parameter | Value |
| --- | --- |
| Nozzle Tag | N14 |
| Nozzle Size | 2 inch |
| Service | Pressure Instrumentation |
| Rating | 300# |
| Orientation | Top of vessel |

2.14.2 Component Configuration

- Nozzle N14 (2")

- HV0012: 2-inch Solenoid Valve - Isolation for transmitter

2.14.3 Instrumentation

- PZT-0001B: Pressure Transmitter - Provides input to 2oo3 voting logic (362-004)

- PI-0001B: Pressure Indicator - Local indication with HH (High-High) alarm

2.14.4 Documentation Discrepancy Note

IMPORTANT: The source documentation contains a contradiction regarding Nozzle N14. In one section, it is described as a 2-inch solenoid valve connection for PZT-0001B. In another section, it is identified as a 3-inch ball valve HV0003. Based on standard P&ID conventions and the detailed instrumentation section, N14 is confirmed as the PZT-0001B pressure transmitter connection. The HV0003 ball valve reference likely belongs to N17. Field verification is recommended.

2.15 Nozzle N15: Pressure Transmitter Connection (PZT-0001C)

Nozzle N15 provides the third pressure measurement for the 2oo3 voting logic safety system.

2.15.1 Nozzle Specifications

| Parameter | Value |
| --- | --- |
| Nozzle Tag | N15 |
| Nozzle Size | 2 inch |
| Service | Pressure Instrumentation |
| Rating | 300# |
| Orientation | Top of vessel |

2.15.2 Component Configuration

- Nozzle N15 (2")

- HV0013: 2-inch Solenoid Valve - Isolation for transmitter

2.15.3 Instrumentation

- PZT-0001C: Pressure Transmitter - Provides input to 2oo3 voting logic (362-004)

- PI-0001C: Pressure Indicator - Local indication with HH (High-High) alarm

2.16 Nozzle N16: Pressure Control Transmitter Connection (PIT-0002/PIC-0002)

Nozzle N16 provides the primary pressure control signal for modulating the pressure control valve PV-0002.

2.16.1 Nozzle Specifications

| Parameter | Value |
| --- | --- |
| Nozzle Tag | N16 |
| Nozzle Size | 2 inch |
| Service | Pressure Control Instrumentation |
| Rating | 300# |
| Orientation | Top of vessel |

2.16.2 Component Configuration

- Nozzle N16 (2")

- HV0014: 2-inch Solenoid Valve - Isolation for transmitter

2.16.3 Instrumentation

- PIT-0002: Pressure Indication Transmitter - Provides process variable signal

- PIC-0002: Pressure Indicating Controller - Controls PV-0002

2.16.4 Control Loop Function

PIC-0002 receives the pressure signal from PIT-0002 and modulates control valve PV-0002 on the 8-inch HP Flare line (Line: 8"-PP01-362-GF0003-B01E9-PP) to maintain vessel pressure within the operating range of 9.0-10.4 barg.

2.16.5 Documentation Discrepancy Note

IMPORTANT: The source documentation contains conflicting information regarding the line number for PV-0002:

- Nozzle N16 description places PV-0002 on line "P8-PP01-61-GF03-B01E9-PP"

- Nozzle N2 description places PV-0002 on line "8"-PP01-362-GF03-B01E9-PP"

These line numbers differ and require clarification. Based on the N2 gas outlet analysis, the correct line designation appears to be 8"-PP01-362-GF0003-B01E9-PP.

2.17 Nozzle N17: Maintenance/Vent Connection

Nozzle N17 is a utility connection for maintenance, venting, or other service requirements.

2.17.1 Nozzle Specifications

| Parameter | Value |
| --- | --- |
| Nozzle Tag | N17 |
| Nozzle Size | 3 inch |
| Service | Maintenance/Vent |
| Rating | 300# |

2.17.2 Component Configuration

- Nozzle N17 (3")

- HV0003: 3-inch Ball Valve - Isolation valve

2.17.3 Termination

The line terminates at the valve (blind end) - used for maintenance access, venting, or future connections. No further downstream piping exists.

2.18 Nozzle N18 (N18A & N18B): Level Gauge Bridle (LG-0001)

Nozzles N18A and N18B form a bridle pair for the local level gauge LG-0001, providing visual indication of vessel liquid level.

2.18.1 Nozzle Specifications

| Parameter | N18A | N18B |
| --- | --- | --- |
| Nozzle Size | 2 inch | 2 inch |
| Service | Level Gauge - Upper | Level Gauge - Lower |
| Rating | 300# | 300# |

2.18.2 Instrumentation

- LG-0001: Level Gauge (Sight Glass type) - Provides local visual indication of liquid level from LLLL (300mm) to HHLL (1300mm)

2.18.3 Component Configuration

N18A Connection Path (Upper):

- Nozzle N18A (2")

- HV0024: 2-inch Solenoid Valve

N18B Connection Path (Lower):

- Nozzle N18B (2")

- HV0025: 2-inch Solenoid Valve

Level Gauge Assembly:

- HV0026: 1-inch Gate Valve - Top of gauge isolation

- LG-0001: Level Gauge (vertical orientation between upper and lower connections)

- HV0027: 1-inch Gate Valve - Bottom of gauge isolation

Instrumentation Line:

- Line Number: 1"-PP01-512-PK0076-B03F9-PP

2.18.4 Header Connection

Piping Specification Change: A 1-inch gate valve separates specification B03F9 from B01M8.

This assembly connects to the Bottom Common Header line 1"-PP01-512-PK0054-B01M8-PP, joining with the N7 and N10 level transmitter assemblies.

SECTION 3: INTERCONNECTED INSTRUMENTATION HEADER SYSTEMS

3.1 Bottom Common Header Network (Liquid Level Instruments)

This header network collects connections from the lower level instruments (N7/LIT-0001, N10/LIT-0003, and N18/LG-0001) and provides common drainage to the liquid outlet system.

3.1.1 Header Line Identification

Main Header Line: 1"-PP01-512-PK0054-B01M8-PP

3.1.2 Connected Instrument Bridles

| Bridle | Nozzles | Instrument | Branch Line Number |
| --- | --- | --- | --- |
| N18 Assembly | N18A, N18B | LG-0001 | 1"-PP01-512-PK0076-B03F9-PP |
| N7 Assembly | N7A, N7B | LIT-0001 | 1"-PP01-512-PK0077-B03F9-PP |
| N10 Assembly | N10A, N10B | LIT-0003 | 1"-PP01-512-PK0078-B03F9-PP |

3.1.3 Header Correlation

The Bottom Common Header correlates with the N3 liquid outlet piping network, specifically connecting near the 4-inch line 4"-PP01-512-PK0006-B01M8-PP. This allows the level instruments to be filled/calibrated and drained through the common liquid handling system.

3.2 Top Common Header Network (Interface Level Instruments)

This header network collects connections from the upper interface level instruments (N6/LZT-0002C, N11/LZT-0002B, and N12/LZT-0002A) and provides common drainage.

3.2.1 Header Line Identification

Main Header Line: 1"-PP01-512-PK0079-B03F9-PP

3.2.2 Connected Instrument Bridles

| Bridle | Nozzles | Instrument | Branch Line Number |
| --- | --- | --- | --- |
| N12 Assembly | N12A, N12B | LZT-0002A | (Direct to header) |
| N11 Assembly | N11A, N11B | LZT-0002B | 1"-PP01-512-PK0080-B03F9-PP |
| N6 Assembly | N6A, N6B | LZT-0002C | 1"-PP01-512-PK0081-B03F9-PP |

3.2.3 Common Header Valves

- HV0052: 1-inch Gate Valve - Main header isolation

- HV0056: 1-inch Drain Valve - Common drain for upper instrument cluster

3.2.4 Header Connection Point

The individual lines from N6, N11, and N12 feed into this header line before the drain valve HV0056. The header then connects to the Bottom Common Header at a 1-inch ball valve tie-in point.

SECTION 4: COMPLETE PIPING LINE LIST

4.1 Process Lines

| Line Number | Size | From | To | Material Spec | Service | Special Requirements |
| --- | --- | --- | --- | --- | --- | --- |
| 16"-PP01-361-GF0014-B03F9-PP | 16" | DS-1 Scrapper (PID-0005-001) | Vessel N5 | B03F9-PP | Fuel Gas Inlet | NO POCKETS (NOTE-10) |
| 16"-PP01-361-GF0031-B03F9-PP | 16" | DS-3 Scrapper (PID-0007-001) | Vessel N4 | B03F9-PP | Fuel Gas Inlet | NO POCKETS (NOTE-10) |
| 14"-PP01-362-GF0001-B01E9-PP | 14" | Vessel N1 | PSV-001 Header | B01E9-PP | PSV Relief | - |
| 14"-PP01-362-GF0004-B01E9-PP | 14" | PSV Header Junction | PSV-002 | B01E9-PP | PSV Relief | - |
| 16"-PP01-362-GF0002-B01E9-PP | 16" | Vessel N2 | Fuel Gas Treatment (PID-0009-001) | B01E9-PP | Main Gas Outlet | - |
| 6"-PP01-362-GF0009-B01E9-PP | 6" | N2 Header Branch | HP Flare via BDV-0001 | B01E9-PP | Blowdown | Spec changes to B01B8 |
| 8"-PP01-362-GF0003-B01E9-PP | 8" | N2 Header Branch | HP Flare via PV-0002 | B01E9-PP | Pressure Control | Spec changes to B01B8 |
| 4"-PP01-512-PK0005-C01N9-PP | 4" | Vessel N3 | EZV-0001 | C01N9-PP | Liquid Outlet | - |
| 4"-PP01-512-PK0006-B01M8-PP | 4" | LV-0001 | Condensate Storage (PID-0024-001) | B01M8-PP | Liquid Outlet | TWO PHASE (NOTE-10) |
| 2"-PP01-567-GF0002-B03F9 | 2" | Vessel N9 | UC | B03F9 | Manual Drain | - |
| 16"-PP01-500-VK0066-B01B8 | 16" | PSV-001 Outlet | HP Flare (PID-0021-001) | B01B8 | Relief | NO POCKETS |
| 16"-PP01-500-VK0008-B01B8 | 16" | PSV-002 Outlet | HP Flare (PID-0021-001) | B01B8 | Relief | NO POCKETS |
| 8"-PP01-500-VK0026-B01B8 | 8" | Blowdown Line | HP Flare (PID-0021-001) | B01B8 | Blowdown | - |
| 10"-PP01-500-VK0010-B01B8 | 10" | PV-0002 Outlet | HP Flare (PID-0021-001) | B01B8 | Pressure Control | - |

4.2 Instrumentation Lines

| Line Number | Size | From | To | Material Spec | Service |
| --- | --- | --- | --- | --- | --- |
| 1"-PP01-512-PK0054-B01M8-PP | 1" | Common Header | N3 System | B01M8-PP | Bottom Level Instruments |
| 1"-PP01-512-PK0076-B03F9-PP | 1" | N18 Assembly | Header | B03F9-PP | LG-0001 |
| 1"-PP01-512-PK0077-B03F9-PP | 1" | N7 Assembly | Header | B03F9-PP | LIT-0001 |
| 1"-PP01-512-PK0078-B03F9-PP | 1" | N10 Assembly | Header | B03F9-PP | LIT-0003 |
| 1"-PP01-512-PK0079-B03F9-PP | 1" | Common Header | Top Instruments | B03F9-PP | Top Level Instruments |
| 1"-PP01-512-PK0080-B03F9-PP | 1" | N11 Assembly | Header | B03F9-PP | LZT-0002B |
| 1"-PP01-512-PK0081-B03F9-PP | 1" | N6 Assembly | Header | B03F9-PP | LZT-0002C |

SECTION 5: COMPLETE VALVE LIST

5.1 Ball Valves

| Tag | Size | Location | Service | Normal Position | Notes |
| --- | --- | --- | --- | --- | --- |
| HV0003 | 3" | Nozzle N17 | Vent/Service | Closed | Terminates at valve |
| HV0004 | 14" | PSV-001 Inlet | PSV Isolation | LO (Locked Open) | - |
| HV0006 | 14" | PSV-002 Inlet | PSV Isolation | LO (Locked Open) | - |
| HV0016 | 8" | PV-0002 Upstream | Pressure Control | Open | - |
| HV0018 | 4" | PV-0002 Bypass | Manual Bypass | Closed | - |
| HV0021 | 10" | PV-0002 Downstream | Pressure Control | Open | - |
| HV0029 | 8" | BDV-0001 Downstream | Blowdown | Closed | - |
| HV0039 | 16" | PSV-001 Outlet | PSV Isolation | Open | - |
| HV0041 | 16" | PSV-002 Outlet | PSV Isolation | Open | Tag duplicated - verify |
| HV0061 | 6" | Blowdown Branch | Blowdown | Closed | - |
| HV0094 | 16" | DS-1 Inlet Line | Inlet Isolation | Open | - |
| HV0203 | 16" | DS-3 Inlet Line | Inlet Isolation | Open | - |

5.2 Gate Valves

| Tag | Size | Location | Service | Normal Position | Notes |
| --- | --- | --- | --- | --- | --- |
| HV0002 | 2" | Nozzle N9 | Manual Drain | NC (Normally Closed) | - |
| HV0026 | 1" | LG-0001 Top | Level Gauge | Open | - |
| HV0027 | 4" | N3 Outlet | Liquid Isolation | Open | Main path |
| HV0027 | 1" | LG-0001 Bottom | Level Gauge | Open | Tag duplicated - verify |
| HV0028 | 4" | N3 Outlet | Liquid Isolation | Open | After EZV-0001 |
| HV0029 | 1" | N7 Assembly | Level Transmitter | Open | - |
| HV0032 | 2" | LV-0001 Bypass | Level Control | Variable | - |
| HV0033 | 1" | N10 Assembly | Level Transmitter | Open | - |
| HV0041 | 1" | N12 Assembly | Level Transmitter | Open | Tag duplicated - verify |
| HV0043 | 1" | N11 Assembly | Level Transmitter | Open | - |
| HV0044 | 1" | N6 Assembly | Level Transmitter | Open | - |
| HV0045 | 1" | N6 Assembly | Level Transmitter | Open | - |
| HV0049 | 1" | N7 Assembly | Level Transmitter | Open | - |
| HV0050 | 1" | N7 Assembly | Level Transmitter | Open | - |
| HV0051 | 1" | N10 Assembly | Level Transmitter | Open | Tag duplicated - verify |
| HV0052 | 1" | Top Header | Header Isolation | Open | - |
| HV0064 | 3" | Nozzle N8 | Maintenance | Closed | - |
| HV0065 | 2" | N3 Outlet | Drain | NC | - |

5.3 Globe Valves

| Tag | Size | Location | Service | Notes |
| --- | --- | --- | --- | --- |
| HV0019 | 4" | PV-0002 Bypass | Throttling | Manual bypass |

5.4 Drain Valves

| Tag | Size | Location | Service |
| --- | --- | --- | --- |
| HV0003 | 1" | N10 Assembly | Instrument Drain |
| HV0005 | 1" | PSV-001 Inlet | Drain |
| HV0007 | 1" | PSV-002 Inlet | Drain |
| HV0017 | 1" | PV-0002 Station | Drain |
| HV0020 | 1" | PV-0002 Station | Drain |
| HV0028 | 1" | N7 Assembly | Instrument Drain |
| HV0038 | 1" | PSV-001 Outlet | Drain |
| HV0040 | 1" | N12 Assembly | Instrument Drain |
| HV0041 | 1" | PSV-002 Outlet | Drain |
| HV0042 | 1" | N11 Assembly | Instrument Drain |
| HV0051 | 1" | N9 Manual Drain | Drain |
| HV0056 | 1" | Top Header | Common Drain |

5.5 Solenoid Valves (2-inch)

| Tag | Location | Instrument Served |
| --- | --- | --- |
| HV0011 | Nozzle N13 | PZT-0001A |
| HV0012 | Nozzle N14 | PZT-0001B |
| HV0013 | Nozzle N15 | PZT-0001C |
| HV0014 | Nozzle N16 | PIT-0002 |
| HV0022 | Nozzle N7A | LIT-0001 |
| HV0023 | Nozzle N7B | LIT-0001 |
| HV0024 | Nozzle N18A | LG-0001 |
| HV0025 | Nozzle N18B | LG-0001 |
| HV0030 | Nozzle N10A | LIT-0003 |
| HV0031 | Nozzle N10B | LIT-0003 |
| HV0034 | Nozzle N6A | LZT-0002C |
| HV0035 | Nozzle N6B | LZT-0002C |
| HV0036 | Nozzle N11A | LZT-0002B |
| HV0037 | Nozzle N11B | LZT-0002B |
| HV0038 | Nozzle N12A | LZT-0002A |
| HV0039 | Nozzle N12B | LZT-0002A |

5.6 Check Valves

| Tag | Size | Location | Service |
| --- | --- | --- | --- |
| (Unnamed) | 16" | DS-1 Inlet Line | Backflow Prevention |
| (Unnamed) | 16" | DS-3 Inlet Line | Backflow Prevention |
| HV0001 | 2" | N9 Drain Line | Backflow Prevention |

5.7 Control Valves

| Tag | Size | Service | Controller | Fail Position |
| --- | --- | --- | --- | --- |
| PV-0002 | 8" | Pressure Control | PIC-0002 | - |
| LV-0001 | 1.5" | Level Control | LIC-0001 | FC |
| BDV-0001 | 6" | Blowdown Control | - | - |
| EZV-0001 | 4" | Emergency Shutdown | SIS | FC |

SECTION 6: COMPLETE INSTRUMENTATION LIST

6.1 Pressure Instruments

| Tag | Type | Location | Function | Voting Logic |
| --- | --- | --- | --- | --- |
| PI-0001A | Pressure Indicator | N13 | Local Indication, HH Alarm | - |
| PI-0001B | Pressure Indicator | N14 | Local Indication, HH Alarm | - |
| PI-0001C | Pressure Indicator | N15 | Local Indication, HH Alarm | - |
| PZT-0001A | Pressure Transmitter | N13 | Safety System | 2oo3 (362-004) |
| PZT-0001B | Pressure Transmitter | N14 | Safety System | 2oo3 (362-004) |
| PZT-0001C | Pressure Transmitter | N15 | Safety System | 2oo3 (362-004) |
| PIT-0002 | Pressure Transmitter | N16 | Process Control | - |
| PIC-0002 | Pressure Controller | N16 | Controls PV-0002 | - |
| PG-0001 | Pressure Gauge | N2 Header | Local Indication | - |

6.2 Level Instruments

| Tag | Type | Location (Nozzles) | Function | Voting Logic |
| --- | --- | --- | --- | --- |
| LG-0001 | Level Gauge | N18A/N18B | Local Visual Indication | - |
| LIT-0001 | Level Transmitter | N7A/N7B | Process Control | - |
| LIT-0003 | Level Transmitter | N10A/N10B | Process Indication | - |
| LIC-0001 | Level Controller | - | Controls LV-0001 | - |
| LZT-0002A | Level Transmitter (GWR) | N12A/N12B | Safety System | 2oo3 (362-003/007) |
| LZT-0002B | Level Transmitter (GWR) | N11A/N11B | Safety System | 2oo3 (362-003/007) |
| LZT-0002C | Level Transmitter (GWR) | N6A/N6B | Safety System | 2oo3 (362-003/007) |
| LI-0002A | Level Indicator | Associated with LZT-0002A | Local Indication | - |
| LI-0002B | Level Indicator | Associated with LZT-0002B | Local Indication | - |
| LI-0002C | Level Indicator | Associated with LZT-0002C | Local Indication | - |
| LV-0002A | Level Valve | Associated with LZT-0002A | - | - |
| LV-0002B | Level Valve | Associated with LZT-0002B | - | - |
| LV-0002C | Level Valve | Associated with LZT-0002C | - | - |

6.3 Corrosion Instruments

| Tag | Type | Location | Function |
| --- | --- | --- | --- |
| CI-0001 | Corrosion Indicator | N3 Outlet Branch | Local Indication |
| CIT-0001 | Corrosion Transmitter | N3 Outlet Branch | Remote Monitoring |

6.4 Safety Relief Devices

| Tag | Type | Set Pressure | Relief Case | Size |
| --- | --- | --- | --- | --- |
| PSV-001 | Pressure Safety Valve | 14.0 barg | DS-3 PCV Failure | 8T10 |
| PSV-002 | Pressure Safety Valve | 14.0 barg | DS-3 PCV Failure | 8T10 |

SECTION 7: CONTROL LOOP DESCRIPTIONS

7.1 Pressure Control Loop (PIC-0002 → PV-0002)

Purpose: Maintains vessel operating pressure within 9.0-10.4 barg range by modulating gas flow to HP Flare.

Loop Components:

- PIT-0002: Pressure transmitter at Nozzle N16 senses vessel pressure

- PIC-0002: Controller compares measured pressure to setpoint

- PV-0002: 8-inch control valve on line 8"-PP01-362-GF0003-B01E9-PP modulates gas flow

Control Action:

- Increasing vessel pressure → PIC-0002 output increases → PV-0002 opens → More gas flows to flare → Pressure decreases

- Decreasing vessel pressure → PIC-0002 output decreases → PV-0002 closes → Less gas flows to flare → Pressure increases

7.2 Level Control Loop (LIC-0001 → LV-0001)

Purpose: Maintains vessel liquid level at Normal Liquid Level (800mm) by modulating liquid discharge.

Loop Components:

- LIT-0001: Level transmitter at Nozzles N7A/N7B senses liquid level

- LIC-0001: Controller compares measured level to NLL setpoint (800mm)

- LV-0001: 1.5-inch control valve on N3 outlet bypass modulates liquid flow

Control Action:

- Rising level → LIC-0001 output increases → LV-0001 opens → More liquid drains → Level decreases

- Falling level → LIC-0001 output decreases → LV-0001 closes → Less liquid drains → Level increases

7.3 High Pressure Safety Instrumented Function (PZT → 2oo3 → ESD)

Purpose: Provides independent high-pressure protection to prevent vessel overpressure.

Loop Components:

- PZT-0001A, PZT-0001B, PZT-0001C: Three independent pressure transmitters

- 2oo3 Voting Logic (362-004): Requires 2 of 3 transmitters to confirm high pressure

- ESD System: Initiates protective actions

Safety Action: When 2 out of 3 transmitters detect pressure above the high-pressure trip setpoint, the voting logic sends a trip signal to the ESD system, which closes EZV-0001 and initiates other protective actions.

7.4 Level Safety Instrumented Function (LZT → 2oo3 → ESD)

Purpose: Provides independent level protection for both high-high and low-low level conditions.

Loop Components:

- LZT-0002A, LZT-0002B, LZT-0002C: Three independent GWR level transmitters

- 2oo3 Voting Logic (362-003 for HHLL, 362-007 for LLLL): Requires 2 of 3 transmitters to confirm level alarm

- ESD System: Initiates protective actions

Safety Actions:

- HHLL (1300mm): Voting logic 362-003 trips to prevent liquid carryover to downstream equipment

- LLLL (300mm): Voting logic 362-007 trips to prevent pump cavitation or loss of seal

SECTION 8: REFERENCE DRAWINGS

| Drawing Number | Title | Connection Point |
| --- | --- | --- |
| N-PG-PP01-PR-PID-0005-001 | DS-1 Scrapper Receiver | Inlet via N5 |
| N-PG-PP01-PR-PID-0007-001 | DS-3 Scrapper Receiver | Inlet via N4 |
| N-PG-PP01-PR-PID-0009-001 | Fuel Gas Treatment Package | Gas Outlet via N2 |
| N-PG-PP01-PR-PID-0021-001 | HP Flare Header | PSV Outlets, Blowdown, Pressure Control |
| N-PG-PP01-PR-PID-0024-001 | Condensate Storage Vessel | Liquid Outlet via N3 |

SECTION 9: NOTES REFERENCE

| Note | Description | Application |
| --- | --- | --- |
| NOTE-2 | Inlet nozzle connection requirements | N4, N5 inlet nozzles |
| NOTE-7 | Design temperature requirements | Vessel design -20°C to 100°C |
| NOTE-10 | NO POCKETS requirement, TWO PHASE designation | Inlet lines, N3 outlet line |

SECTION 10: DOCUMENTATION DISCREPANCIES AND UNCERTAINTIES

The following items have been identified as requiring field verification or clarification due to contradictions or ambiguities in the source documentation:

10.1 Tag Number Duplications

| Duplicated Tag | Locations | Recommended Action |
| --- | --- | --- |
| HV0004 | PSV-001 inlet (14" Ball) AND N3 bypass (1.5" Ball) | Field verify - assign unique tags |
| HV0027 | N3 outlet (4" Gate) AND LG-0001 bottom (1" Gate) | Field verify - assign unique tags |
| HV0028 | N3 outlet (4" Gate) AND N7 drain (1" Drain) | Field verify - assign unique tags |
| HV0029 | BDV downstream (8" Ball) AND N7 assembly (1" Gate) AND N3 bypass (1.5" valve) | Field verify - assign unique tags |
| HV0030 | N10A solenoid (2") AND N3 bypass (1.5" valve with 0.5" drain) | Field verify - assign unique tags |
| HV0038 | PSV-001 drain (1") AND N12A solenoid (2") | Field verify - assign unique tags |
| HV0039 | PSV-001 outlet (16" Ball) AND N12B solenoid (2") | Field verify - assign unique tags |
| HV0041 | PSV-002 outlet (16" Ball) AND PSV-002 drain (1") AND N12 assembly (1" Gate) | Field verify - assign unique tags |
| HV0051 | N9 drain (1") AND N10 assembly (1" Gate) | Field verify - assign unique tags |

10.2 Nozzle N14 Discrepancy

Issue: Source documentation states N14 is both:

- A 2-inch solenoid valve connection for PZT-0001B (instrumentation section)

- A 3-inch ball valve HV0003 (end of one document section)

Resolution Applied: Based on P&ID conventions and detailed instrumentation descriptions, N14 is documented as the PZT-0001B connection. HV0003 (3" ball valve) is assigned to N17.

Recommended Action: Field walk-down to confirm N14 configuration.

10.3 PV-0002 Line Number Discrepancy

Issue: Two different line numbers cited for PV-0002 location:

- "P8-PP01-61-GF03-B01E9-PP" (Nozzle N16 section)

- "8"-PP01-362-GF03-B01E9-PP" (Nozzle N2 section)

Resolution Applied: Line designation 8"-PP01-362-GF0003-B01E9-PP used based on N2 gas outlet analysis.

Recommended Action: Verify correct line number in field.

10.4 Items Requiring Confirmation

| Item | Uncertainty | Recommended Action |
| --- | --- | --- |
| Vessel OD | Source states "OD 5500" which conflicts with ID 2200mm and Length 5500mm | Confirm vessel dimensions |
| Design Temperature | One source says "-23°C to 72°C", another says "-20°C to 100°C" | Verify from vessel nameplate |
| Check Valve Tags | Inlet check valves on DS-1 and DS-3 lines have no tags assigned | Assign tags or confirm unnamed |
| LV-0002A/B/C | Associated with LZT transmitters but exact location unclear | Field verify installation |

SECTION 11: COMPLETE NOZZLE SUMMARY TABLE

| Nozzle | Size | Service | Primary Equipment | Key Valves | Line Number |
| --- | --- | --- | --- | --- | --- |
| N1 | 14" | PSV Relief Header | PSV-001, PSV-002 | HV0004, HV0006 | 14"-PP01-362-GF0001-B01E9-PP |
| N2 | 16" | Gas Outlet | PV-0002, BDV-0001 | HV0015, HV0016, HV0061 | 16"-PP01-362-GF0002-B01E9-PP |
| N3 | 4" | Liquid Outlet | EZV-0001, LV-0001 | HV0027, HV0028, HV0065 | 4"-PP01-512-PK0005-C01N9-PP |
| N4 | 12" | Gas Inlet (DS-3) | - | HV0203, Check Valve | 16"-PP01-361-GF0031-B03F9-PP |
| N5 | 12" | Gas Inlet (DS-1) | - | HV0094, Check Valve | 16"-PP01-361-GF0014-B03F9-PP |
| N6A/N6B | 2" | Level Bridle | LZT-0002C | HV0034, HV0035, HV0044, HV0045 | 1"-PP01-512-PK0081-B03F9-PP |
| N7A/N7B | 2" | Level Bridle | LIT-0001 | HV0022, HV0023, HV0029 | 1"-PP01-512-PK0077-B03F9-PP |
| N8 | 3" | Maintenance | - | HV0064 | - |
| N9 | 2" | Manual Drain | UC | HV0002, HV0001, HV0051 | 2"-PP01-567-GF0002-B03F9 |
| N10A/N10B | 2" | Level Bridle | LIT-0003 | HV0030, HV0031, HV0033 | 1"-PP01-512-PK0078-B03F9-PP |
| N11A/N11B | 2" | Level Bridle | LZT-0002B | HV0036, HV0037, HV0042, HV0043 | 1"-PP01-512-PK0080-B03F9-PP |
| N12A/N12B | 2" | Level Bridle | LZT-0002A | HV0038, HV0039, HV0040, HV0041 | - |
| N13 | 2" | Pressure Instr. | PZT-0001A, PI-0001A | HV0011 | - |
| N14 | 2" | Pressure Instr. | PZT-0001B, PI-0001B | HV0012 | - |
| N15 | 2" | Pressure Instr. | PZT-0001C, PI-0001C | HV0013 | - |
| N16 | 2" | Pressure Control | PIT-0002, PIC-0002 | HV0014 | - |
| N17 | 3" | Vent/Service | - | HV0003 | Terminates |
| N18A/N18B | 2" | Level Gauge | LG-0001 | HV0024, HV0025, HV0026, HV0027 | 1"-PP01-512-PK0076-B03F9-PP |

This comprehensive document provides all necessary information to recreate the P&ID in complete detail, including every equipment item, instrument, valve, line, nozzle connection, and control loop. All identified discrepancies and uncertainties have been documented for field verification.

For the dublication give them the specific name

COMPREHENSIVE P&ID RECONSTRUCTION DOCUMENT

Fuel Gas Knockout Drum System (PP01-362-V001)

Complete Technical Specification with Resolved Tag Duplications

SECTION 1: MAIN EQUIPMENT SPECIFICATIONS

1.1 Fuel Gas Knockout Drum (PP01-362-V001)

The central process vessel is a horizontal knockout drum designed to remove entrained liquids from fuel gas streams originating from the DS-1 and DS-3 scrapper receivers. The vessel separates liquid droplets from the gas phase through gravity settling and velocity reduction before the gas proceeds to the Fuel Gas Treatment Package.

1.1.1 Equipment Identification

| Parameter | Value |
| --- | --- |
| Equipment Tag | PP01-362-V001 |
| Operating Tag | 362-V001 |
| Service | Fuel Gas Knockout Drum |
| Vessel Type | Horizontal Cylindrical Drum |

1.1.2 Dimensional Data

| Parameter | Value |
| --- | --- |
| Internal Diameter (ID) | 2200 mm |
| Length (Tangent to Tangent) | 5500 mm |
| Orientation | Horizontal |

1.1.3 Design Conditions

| Parameter | Value |
| --- | --- |
| Design Pressure | 14 barg |
| Design Temperature | -20°C to 100°C (NOTE-7) |
| Operating Pressure | 9.0 to 10.4 barg |
| Operating Temperature | 23°C to 72°C |

1.1.4 Material and Construction

| Parameter | Value |
| --- | --- |
| Shell Material | Carbon Steel (CS) |
| Corrosion Allowance | 3 mm |
| Internal Coating | Epoxy Ceramic Coating |
| External Insulation | None |
| Trim Number | PP01-362-V001-TX0001-B03F9 |

1.1.5 Vessel Internals

The vessel contains a mist eliminator designated as MW 24" (24-inch Mist Wire mesh demister pad). This wire mesh pad is positioned in the gas flow path upstream of the gas outlet nozzle N2. The demister captures entrained liquid droplets from the gas stream before the gas exits the vessel, improving separation efficiency.

1.1.6 Level Settings

| Level Designation | Height from Vessel Bottom | Function |
| --- | --- | --- |
| HHLL (High-High Liquid Level) | 1300 mm | Alarm and Trip |
| HLL (High Liquid Level) | 1150 mm | Alarm |
| NLL (Normal Liquid Level) | 800 mm | Normal Operating Level |
| LLL (Low Liquid Level) | 450 mm | Alarm |
| LLLL (Low-Low Liquid Level) | 300 mm | Alarm and Trip |

SECTION 2: COMPLETE NOZZLE SCHEDULE AND CONNECTIONS

2.1 Nozzle N1: Pressure Safety Valve (PSV) Header Connection

Nozzle N1 is the primary pressure relief connection point, serving as the common inlet header for two parallel Pressure Safety Valves (PSV-001 and PSV-002) that protect the vessel from overpressure conditions.

2.1.1 Nozzle Specifications

| Parameter | Value |
| --- | --- |
| Nozzle Tag | N1 |
| Nozzle Size | 14 inch |
| Service | PSV Relief Header |
| Rating | 300# |
| Orientation | Top of vessel |

2.1.2 Main Header Line from Nozzle N1

The main relief header line originates at nozzle N1 with designation 14"-PP01-362-GF0001-B01E9-PP. This 14-inch line serves as the common supply header for both PSV branches.

From nozzle N1, the 14-inch main header runs horizontally. At the first junction point, a parallel branch line designated 14"-PP01-362-GF0004-B01E9-PP splits off to feed PSV-002, while the main header continues to PSV-001.

2.1.3 PSV-001 Flow Path (Complete Component Sequence)

Starting from the main header line 14"-PP01-362-GF0001-B01E9-PP:

- HV0004-PSV1-INLET: 14-inch Ball Valve - Inlet isolation valve for PSV-001, maintained in Locked Open (LO) position during normal operation

- HV0005-PSV1-DRAIN: 1-inch Drain Valve - Located between HV0004-PSV1-INLET and the inlet reducer, provides drainage capability for the inlet piping

- Reducer: Concentric reducer 14" × 8" - Reduces line size from 14 inches to 8 inches to match PSV inlet connection

- PSV-001: Pressure Safety Valve

  - Set Pressure: 14.0 barg

  - Relief Case: DS-3 PCV Failure

  - Orifice Size: 8T10

- Reducer: Concentric reducer 10" × 16" - Expands from PSV outlet to 16-inch flare header

- HV0038-PSV1-OUTLET-DRAIN: 1-inch Drain Valve - Located between PSV outlet reducer and HV0039-PSV1-OUTLET

- HV0039-PSV1-OUTLET: 16-inch Ball Valve - Outlet isolation valve

Outlet Line: 16"-PP01-500-VK0066-B01B8 routes to HP Flare Header (Drawing N-PG-PP01-PR-PID-0021-001)

2.1.4 PSV-002 Flow Path (Complete Component Sequence)

Starting from the branch line 14"-PP01-362-GF0004-B01E9-PP:

- HV0006-PSV2-INLET: 14-inch Ball Valve - Inlet isolation valve for PSV-002, maintained in Locked Open (LO) position during normal operation

- HV0007-PSV2-DRAIN: 1-inch Drain Valve - Located between HV0006-PSV2-INLET and the inlet reducer

- Reducer: Concentric reducer 14" × 8" - Reduces line size from 14 inches to 8 inches

- PSV-002: Pressure Safety Valve

  - Set Pressure: 14.0 barg

  - Relief Case: DS-3 PCV Failure

  - Orifice Size: 8T10

- Reducer: Concentric reducer 10" × 16" - Expands from PSV outlet

- HV0040-PSV2-OUTLET-DRAIN: 1-inch Drain Valve - Located between PSV outlet reducer and outlet ball valve

- HV0041-PSV2-OUTLET: 16-inch Ball Valve - Outlet isolation valve

Outlet Line: 16"-PP01-500-VK0008-B01B8 routes to HP Flare Header (Drawing N-PG-PP01-PR-PID-0021-001)

2.1.5 PSV Data Summary Table

| Parameter | PSV-001 | PSV-002 |
| --- | --- | --- |
| Tag | PSV-001 | PSV-002 |
| Set Pressure | 14.0 barg | 14.0 barg |
| Relief Case | DS-3 PCV Failure | DS-3 PCV Failure |
| Orifice Size | 8T10 | 8T10 |
| Inlet Size | 8" (via 14"×8" reducer) | 8" (via 14"×8" reducer) |
| Outlet Size | 10" (to 16" via reducer) | 10" (to 16" via reducer) |
| Inlet Isolation | HV0004-PSV1-INLET (14" Ball, LO) | HV0006-PSV2-INLET (14" Ball, LO) |
| Outlet Isolation | HV0039-PSV1-OUTLET (16" Ball) | HV0041-PSV2-OUTLET (16" Ball) |
| Inlet Drain | HV0005-PSV1-DRAIN (1") | HV0007-PSV2-DRAIN (1") |
| Outlet Drain | HV0038-PSV1-OUTLET-DRAIN (1") | HV0040-PSV2-OUTLET-DRAIN (1") |

2.2 Nozzle N2: Main Gas Outlet

Nozzle N2 is the primary gas outlet from the vessel, located at the top of the drum. Gas exits through this nozzle after passing through the internal mist eliminator (MW 24"). The outlet system splits into three distinct flow paths serving different functions.

2.2.1 Nozzle Specifications

| Parameter | Value |
| --- | --- |
| Nozzle Tag | N2 |
| Nozzle Size | 16 inch |
| Service | Main Gas Outlet |
| Rating | 300# |
| Orientation | Top of vessel |

2.2.2 Primary Outlet Header

From nozzle N2, the main gas outlet line is designated 16"-PP01-362-GF0002-B01E9-PP. Immediately at the nozzle, the following components are installed:

- Blind Flange: 16-inch blind flange for isolation capability

- PG-0001: Pressure Gauge - Local pressure indication

- HV0015-N2-PG: Isolation valve for pressure gauge connection

The 16-inch header then splits into three distinct paths:

2.2.3 Path 1: Fuel Gas Treatment Package (Main Process Flow)

The primary process flow continues as the 16-inch main line 16"-PP01-362-GF0002-B01E9-PP routing directly to the Fuel Gas Treatment Package.

Destination: Fuel Gas Treatment Package (Drawing N-PG-PP01-PR-PID-0009-001)

This is the normal operating flow path for treated fuel gas exiting the knockout drum.

2.2.4 Path 2: Blowdown/Depressurization to HP Flare

A 6-inch branch line provides blowdown and depressurization capability:

Line Designation: 6"-PP01-362-GF0009-B01E9-PP

Component sequence from the branch point:

- HV0061-BLOWDOWN: 6-inch Ball Valve - Blowdown isolation valve

- BDV-0001: Control Valve (Blowdown Valve) - Automated blowdown control

- Reducer: 6" to 8" expander

- HV0029-BLOWDOWN-OUTLET: 8-inch Ball Valve - Downstream isolation

Piping Specification Change: At the reducer/HV0029-BLOWDOWN-OUTLET location, the piping specification changes from B01E9 to B01B8.

Exit Line: 8"-PP01-500-VK0026-B01B8 routing to HP Flare Header (Drawing N-PG-PP01-PR-PID-0021-001)

2.2.5 Path 3: Pressure Control to HP Flare

An 8-inch branch line provides continuous pressure control capability:

Line Designation: 8"-PP01-362-GF0003-B01E9-PP

Main Control Path Component Sequence:

- HV0016-PV-INLET: 8-inch Ball Valve - Upstream isolation

- HV0017-PV-DRAIN-UP: 1-inch Drain Valve - Located between HV0016-PV-INLET and PV-0002

- PV-0002: Pressure Control Valve (Globe type) - Main pressure control valve receiving signal from PIC-0002

- HV0020-PV-DRAIN-DN: 1-inch Drain Valve - Located downstream of PV-0002

- Reducer: 8" to 10" expander

- HV0021-PV-OUTLET: 10-inch Ball Valve - Downstream isolation

Bypass Path (Parallel to PV-0002):

A 4-inch bypass line runs parallel to the main control valve for manual override or maintenance bypass:

- HV0018-PV-BYPASS-IN: 4-inch Ball Valve - Bypass inlet isolation

- HV0019-PV-BYPASS-OUT: 4-inch Globe Valve - Bypass throttling/isolation

Piping Specification Change: At the HV0021-PV-OUTLET location, the piping specification changes from B01E9 to B01B8.

Exit Line: 10"-PP01-500-VK0010-B01B8 routing to HP Flare Header (Drawing N-PG-PP01-PR-PID-0021-001)

2.3 Nozzle N3: Condensate/Liquid Outlet

Nozzle N3 is located at the bottom of the vessel and serves as the primary liquid outlet for separated condensate. The liquid is routed to the Condensate Storage Vessel.

2.3.1 Nozzle Specifications

| Parameter | Value |
| --- | --- |
| Nozzle Tag | N3 |
| Nozzle Size | 4 inch |
| Service | Condensate Liquid Outlet |
| Rating | 300# |
| Orientation | Bottom of vessel |

2.3.2 Main Outlet Line Configuration

Line Designation: 4"-PP01-512-PK0005-C01N9-PP (originating at nozzle, specification starts as C01N9)

The line transitions to 4"-PP01-512-PK0006-B01M8-PP downstream.

Destination: Condensate Storage Vessel (Drawing N-PG-PP01-PR-PID-0024-001)

2.3.3 Main Flow Path Component Sequence

From nozzle N3, the main liquid control path includes:

- HV0065-N3-DRAIN: 2-inch Gate Valve (Normally Closed) - Drain valve located immediately at the nozzle

- HV0027-N3-INLET-ISO: 4-inch Gate Valve - Primary upstream isolation

- EZV-0001: Emergency Shutdown Valve - 4-inch automated isolation valve for emergency shutoff

- HV0028-N3-OUTLET-ISO: 4-inch Gate Valve - Primary downstream isolation

2.3.4 Level Control Bypass Path

A bypass path exists parallel to the main EZV-0001 valve for level control during normal operation. This bypass branches off before EZV-0001 and rejoins after HV0028-N3-OUTLET-ISO:

Bypass Entry Point: Junction with HV0032-LV-BYPASS-IN (2-inch valve)

Bypass Component Sequence:

- HV0032-LV-BYPASS-IN: 2-inch Gate Valve - Bypass inlet isolation

- Reducer: 2" to 1.5" reducer

- HV0004-LV-BYPASS: 1.5-inch Ball Valve - Bypass isolation

- HV0029-LV-INLET: 1.5-inch Valve - LV-0001 inlet isolation

- LV-0001: Level Control Valve - 1.5-inch control valve receiving signal from LIC-0001

- HV0030-LV-OUTLET: 1.5-inch Valve - LV-0001 outlet isolation

- HV0030-LV-DRAIN: 0.5-inch Drain Valve - Located at low point near LV-0001

- Reducer: 1.5" to 4" expander

- Rejoins main 4-inch line before final destination

2.3.5 Instrumentation Connection

A 2-inch blind flange branch connection from the outlet line provides instrumentation access:

- CIT-0001: Corrosion Indication Transmitter

- CI-0001: Corrosion Indicator

These instruments monitor corrosion in the liquid outlet piping.

2.3.6 Service Designation

The 4-inch outlet line is designated as TWO PHASE per NOTE-10, indicating it carries both liquid and some entrained gas.

2.4 Nozzle N4: Fuel Gas Inlet (From DS-3 Scrapper Receiver)

Nozzle N4 receives fuel gas from the DS-3 Scrapper Receiver system. This is one of two primary inlet connections to the knockout drum.

2.4.1 Nozzle Specifications

| Parameter | Value |
| --- | --- |
| Nozzle Tag | N4 |
| Nozzle Size | 12 inch |
| Service | Fuel Gas Inlet from DS-3 |
| Rating | 300# |
| Orientation | Top of vessel |

2.4.2 Inlet Line Configuration

Source Drawing: N-PG-PP01-PR-PID-0007-001 (DS-3 Scrapper Receiver)

Line Designation: 16"-PP01-361-GF0031-B03F9-PP

Special Requirement: NO POCKETS (NOTE-10) - The line must be self-draining with no low points where liquid can accumulate.

2.4.3 Component Sequence (From Source to Vessel)

Following the flow direction from the DS-3 Scrapper Receiver toward the vessel:

- Line Origin: 16-inch line exits Drawing N-PG-PP01-PR-PID-0007-001

- CV-N4-INLET: 16-inch Check Valve - Prevents backflow toward the scrapper receiver

- HV0203-N4-INLET: 16-inch Ball Valve - Main inlet isolation valve

- Reducer: Concentric reducer 16" to 12" - Reduces line size to match nozzle N4

- Nozzle N4: 12-inch vessel nozzle connection

2.4.4 Connection Notes

- NOTE-2 applies to this nozzle connection specifying installation requirements

- The check valve and ball valve arrangement allows isolation of the inlet while preventing reverse flow during upset conditions

2.5 Nozzle N5: Fuel Gas Inlet (From DS-1 Scrapper Receiver)

Nozzle N5 receives fuel gas from the DS-1 Scrapper Receiver system. This is the second primary inlet connection to the knockout drum.

2.5.1 Nozzle Specifications

| Parameter | Value |
| --- | --- |
| Nozzle Tag | N5 |
| Nozzle Size | 12 inch |
| Service | Fuel Gas Inlet from DS-1 |
| Rating | 300# |
| Orientation | Top of vessel |

2.5.2 Inlet Line Configuration

Source Drawing: N-PG-PP01-PR-PID-0005-001 (DS-1 Scrapper Receiver)

Line Designation: 16"-PP01-361-GF0014-B03F9-PP

Special Requirement: NO POCKETS (NOTE-10) - The line must be self-draining.

2.5.3 Component Sequence (From Source to Vessel)

Following the flow direction from the DS-1 Scrapper Receiver toward the vessel:

- Line Origin: 16-inch line exits Drawing N-PG-PP01-PR-PID-0005-001

- CV-N5-INLET: 16-inch Check Valve - Prevents backflow toward the scrapper receiver

- HV0094-N5-INLET: 16-inch Ball Valve - Main inlet isolation valve

- Reducer: Concentric reducer 16" to 12" - Reduces line size to match nozzle N5

- Nozzle N5: 12-inch vessel nozzle connection

2.5.4 Connection Notes

- NOTE-2 applies to this nozzle connection specifying installation requirements

- Configuration mirrors N4 inlet for operational consistency

2.6 Nozzle N6 (N6A & N6B): Level Transmitter Bridle (LZT-0002C)

Nozzles N6A and N6B form a bridle pair for level transmitter LZT-0002C. This is part of the upper interface level measurement system.

2.6.1 Nozzle Specifications

| Parameter | N6A | N6B |
| --- | --- | --- |
| Nozzle Size | 2 inch | 2 inch |
| Service | Level Bridle - Upper | Level Bridle - Lower |
| Rating | 300# | 300# |

2.6.2 Instrumentation

- LZT-0002C: Level Transmitter (Guided Wave Radar type)

- Part of 2oo3 voting logic for safety level measurement

2.6.3 Component Configuration

N6A Connection Path:

- Nozzle N6A (2")

- HV0034-N6A-SOL: 2-inch Solenoid Valve - Upper isolation

N6B Connection Path:

- Nozzle N6B (2")

- HV0035-N6B-SOL: 2-inch Solenoid Valve - Lower isolation

Common Instrumentation Line:

- Line Number: 1"-PP01-512-PK0081-B03F9-PP

- HV0044-N6-GATE-UP: 1-inch Gate Valve - Upstream of LZT-0002C

- 2-inch Blind Flange: Located before HV0044-N6-GATE-UP for instrument access

- HV0045-N6-GATE-DN: 1-inch Gate Valve - Downstream isolation

2.6.4 Header Connection

This bridle connects to the Top Common Header line 1"-PP01-512-PK0079-B03F9-PP, joining before the common drain valve HV0056-TOP-HDR-DRAIN.

2.7 Nozzle N7 (N7A & N7B): Level Transmitter Bridle (LIT-0001)

Nozzles N7A and N7B form a bridle pair for level indicating transmitter LIT-0001. This provides primary level measurement for process control.

2.7.1 Nozzle Specifications

| Parameter | N7A | N7B |
| --- | --- | --- |
| Nozzle Size | 2 inch | 2 inch |
| Service | Level Bridle - Upper | Level Bridle - Lower |
| Rating | 300# | 300# |

2.7.2 Instrumentation

- LIT-0001: Level Indicating Transmitter - Primary level measurement for LIC-0001 controller

2.7.3 Component Configuration

N7A Connection Path:

- Nozzle N7A (2")

- HV0022-N7A-SOL: 2-inch Solenoid Valve - Upper isolation

- HV0028-N7-DRAIN: 1-inch Drain Valve - Located upstream of HV0022-N7A-SOL

N7B Connection Path:

- Nozzle N7B (2")

- HV0023-N7B-SOL: 2-inch Solenoid Valve - Lower isolation

Common Instrumentation Line:

- Line Number: 1"-PP01-512-PK0077-B03F9-PP

- HV0029-N7-GATE: 1-inch Gate Valve - After N7A connection junction

- HV0049-N7-GATE-2: 1-inch Gate Valve

- HV0050-N7-GATE-3: 1-inch Gate Valve - Further downstream

2.7.4 Header Connection

This bridle connects to the Bottom Common Header line 1"-PP01-512-PK0054-B01M8-PP, which correlates with the N3 liquid outlet piping system.

2.8 Nozzle N8: Service/Maintenance Connection

Nozzle N8 is a standalone service connection for maintenance, drainage, or utility access.

2.8.1 Nozzle Specifications

| Parameter | Value |
| --- | --- |
| Nozzle Tag | N8 |
| Nozzle Size | 3 inch |
| Service | Maintenance/Service |
| Rating | 300# |

2.8.2 Component Configuration

- HV0064-N8-SERVICE: 3-inch Gate Valve - Direct connection to nozzle for isolation

No further downstream piping is detailed; the valve provides isolation for maintenance access to the vessel.

2.9 Nozzle N9: Manual Drain to UC (Utility Connection)

Nozzle N9 provides a manual drain connection from the vessel bottom to a utility containment structure (UC).

2.9.1 Nozzle Specifications

| Parameter | Value |
| --- | --- |
| Nozzle Tag | N9 |
| Nozzle Size | 2 inch |
| Service | Manual Drain |
| Rating | 300# |
| Orientation | Bottom of vessel |

2.9.2 Line Configuration

Line Designation: 2"-PP01-567-GF0002-B03F9

Destination: UC (Utility Connection - described as bucket/pit type containment structure)

2.9.3 Component Sequence (From Nozzle to UC)

- Nozzle N9 (2")

- HV0002-N9-ISO: 2-inch Gate Valve - Primary isolation (Normally Closed position)

- HV0051-N9-DRAIN: 1-inch Drain Valve - Located between HV0002-N9-ISO and check valve

- HV0001-N9-CHECK: 2-inch Check Valve - Prevents backflow from UC to vessel

- Reducer: 2" to 0.75" reducer

- UC: Utility Connection termination point

2.10 Nozzle N10 (N10A & N10B): Level Transmitter Bridle (LIT-0003)

Nozzles N10A and N10B form a bridle pair for level indicating transmitter LIT-0003.

2.10.1 Nozzle Specifications

| Parameter | N10A | N10B |
| --- | --- | --- |
| Nozzle Size | 2 inch | 2 inch |
| Service | Level Bridle - Upper | Level Bridle - Lower |
| Rating | 300# | 300# |

2.10.2 Instrumentation

- LIT-0003: Level Indicating Transmitter

2.10.3 Component Configuration

N10A Connection Path:

- Nozzle N10A (2")

- HV0030-N10A-SOL: 2-inch Solenoid Valve

- HV0003-N10-DRAIN: 1-inch Drain Valve - Located before HV0030-N10A-SOL

N10B Connection Path:

- Nozzle N10B (2")

- HV0031-N10B-SOL: 2-inch Solenoid Valve

Common Instrumentation Line:

- Line Number: 1"-PP01-512-PK0078-B03F9-PP

- 2-inch Blind Flange: Located before LIT-0003 instrument

- HV0033-N10-GATE: 1-inch Gate Valve - After N10B connection

- HV0051-N10-GATE: 1-inch Gate Valve - Further downstream

2.10.4 Header Connection

Piping Specification Change: At a junction point, the specification changes from B03F9 to B01M8.

This bridle connects to the Bottom Common Header line 1"-PP01-512-PK0054-B01M8-PP, joining with N7 and N18 assemblies.

2.11 Nozzle N11 (N11A & N11B): Level Transmitter Bridle (LZT-0002B)

Nozzles N11A and N11B form a bridle pair for level transmitter LZT-0002B, part of the safety level measurement system.

2.11.1 Nozzle Specifications

| Parameter | N11A | N11B |
| --- | --- | --- |
| Nozzle Size | 2 inch | 2 inch |
| Service | Level Bridle - Upper | Level Bridle - Lower |
| Rating | 300# | 300# |

2.11.2 Instrumentation

- LZT-0002B: Level Transmitter (Guided Wave Radar type)

- Part of 2oo3 voting logic for safety level measurement

- Associated with LI-0002B (Level Indicator) and LV-0002B (Level Valve)

2.11.3 Component Configuration

N11A Connection Path:

- Nozzle N11A (2")

- HV0036-N11A-SOL: 2-inch Solenoid Valve

N11B Connection Path:

- Nozzle N11B (2")

- HV0037-N11B-SOL: 2-inch Solenoid Valve

Common Instrumentation Line:

- Line Number: 1"-PP01-512-PK0080-B03F9-PP

- HV0042-N11-DRAIN: 1-inch Drain Valve - Between LZT instrument and N11A junction

- 2-inch Blind Flange: Located between line and LZT instrument

- HV0043-N11-GATE: 1-inch Gate Valve - After N11B connection

2.11.4 Header Connection

This bridle connects to the Top Common Header line 1"-PP01-512-PK0079-B03F9-PP, joining before the common drain valve HV0056-TOP-HDR-DRAIN.

2.12 Nozzle N12 (N12A & N12B): Level Transmitter Bridle (LZT-0002A)

Nozzles N12A and N12B form a bridle pair for level transmitter LZT-0002A, part of the safety level measurement system.

2.12.1 Nozzle Specifications

| Parameter | N12A | N12B |
| --- | --- | --- |
| Nozzle Size | 2 inch | 2 inch |
| Service | Level Bridle - Upper | Level Bridle - Lower |
| Rating | 300# | 300# |

2.12.2 Instrumentation

- LZT-0002A: Level Transmitter (Guided Wave Radar type)

- Part of 2oo3 voting logic for safety level measurement

- Associated with LI-0002A (Level Indicator) and LV-0002A (Level Valve)

2.12.3 Component Configuration

N12A Connection Path:

- Nozzle N12A (2")

- HV0038-N12A-SOL: 2-inch Solenoid Valve

N12B Connection Path:

- Nozzle N12B (2")

- HV0039-N12B-SOL: 2-inch Solenoid Valve

Common Instrumentation Line:

- HV0040-N12-DRAIN: 1-inch Drain Valve - At junction between N12A connection and LZT instrument

- 2-inch Blind Flange: Located before drain valve

- HV0041-N12-GATE: 1-inch Gate Valve - On connection line between N12A and N12B

2.12.4 Header Connection

This bridle connects to the Top Common Header line 1"-PP01-512-PK0079-B03F9-PP, connecting near the 1-inch gate valve HV0052-TOP-HDR-ISO.

2.13 Nozzle N13: Pressure Transmitter Connection (PZT-0001A)

Nozzle N13 provides the first pressure measurement for the 2oo3 voting logic safety system.

2.13.1 Nozzle Specifications

| Parameter | Value |
| --- | --- |
| Nozzle Tag | N13 |
| Nozzle Size | 2 inch |
| Service | Pressure Instrumentation |
| Rating | 300# |
| Orientation | Top of vessel |

2.13.2 Component Configuration

- Nozzle N13 (2")

- HV0011-N13-SOL: 2-inch Solenoid Valve - Isolation for transmitter

2.13.3 Instrumentation

- PZT-0001A: Pressure Transmitter - Provides input to 2oo3 voting logic (362-004)

- PI-0001A: Pressure Indicator - Local indication with HH (High-High) alarm

2.14 Nozzle N14: Pressure Transmitter Connection (PZT-0001B)

Nozzle N14 provides the second pressure measurement for the 2oo3 voting logic safety system.

2.14.1 Nozzle Specifications

| Parameter | Value |
| --- | --- |
| Nozzle Tag | N14 |
| Nozzle Size | 2 inch |
| Service | Pressure Instrumentation |
| Rating | 300# |
| Orientation | Top of vessel |

2.14.2 Component Configuration

- Nozzle N14 (2")

- HV0012-N14-SOL: 2-inch Solenoid Valve - Isolation for transmitter

2.14.3 Instrumentation

- PZT-0001B: Pressure Transmitter - Provides input to 2oo3 voting logic (362-004)

- PI-0001B: Pressure Indicator - Local indication with HH (High-High) alarm

2.15 Nozzle N15: Pressure Transmitter Connection (PZT-0001C)

Nozzle N15 provides the third pressure measurement for the 2oo3 voting logic safety system.

2.15.1 Nozzle Specifications

| Parameter | Value |
| --- | --- |
| Nozzle Tag | N15 |
| Nozzle Size | 2 inch |
| Service | Pressure Instrumentation |
| Rating | 300# |
| Orientation | Top of vessel |

2.15.2 Component Configuration

- Nozzle N15 (2")

- HV0013-N15-SOL: 2-inch Solenoid Valve - Isolation for transmitter

2.15.3 Instrumentation

- PZT-0001C: Pressure Transmitter - Provides input to 2oo3 voting logic (362-004)

- PI-0001C: Pressure Indicator - Local indication with HH (High-High) alarm

2.16 Nozzle N16: Pressure Control Transmitter Connection (PIT-0002/PIC-0002)

Nozzle N16 provides the primary pressure control signal for modulating the pressure control valve PV-0002.

2.16.1 Nozzle Specifications

| Parameter | Value |
| --- | --- |
| Nozzle Tag | N16 |
| Nozzle Size | 2 inch |
| Service | Pressure Control Instrumentation |
| Rating | 300# |
| Orientation | Top of vessel |

2.16.2 Component Configuration

- Nozzle N16 (2")

- HV0014-N16-SOL: 2-inch Solenoid Valve - Isolation for transmitter

2.16.3 Instrumentation

- PIT-0002: Pressure Indication Transmitter - Provides process variable signal

- PIC-0002: Pressure Indicating Controller - Controls PV-0002

2.16.4 Control Loop Function

PIC-0002 receives the pressure signal from PIT-0002 and modulates control valve PV-0002 on the 8-inch HP Flare line (Line: 8"-PP01-362-GF0003-B01E9-PP) to maintain vessel pressure within the operating range of 9.0-10.4 barg.

2.17 Nozzle N17: Maintenance/Vent Connection

Nozzle N17 is a utility connection for maintenance, venting, or other service requirements.

2.17.1 Nozzle Specifications

| Parameter | Value |
| --- | --- |
| Nozzle Tag | N17 |
| Nozzle Size | 3 inch |
| Service | Maintenance/Vent |
| Rating | 300# |

2.17.2 Component Configuration

- Nozzle N17 (3")

- HV0003-N17-VENT: 3-inch Ball Valve - Isolation valve

2.17.3 Termination

The line terminates at the valve (blind end) - used for maintenance access, venting, or future connections. No further downstream piping exists.

2.18 Nozzle N18 (N18A & N18B): Level Gauge Bridle (LG-0001)

Nozzles N18A and N18B form a bridle pair for the local level gauge LG-0001, providing visual indication of vessel liquid level.

2.18.1 Nozzle Specifications

| Parameter | N18A | N18B |
| --- | --- | --- |
| Nozzle Size | 2 inch | 2 inch |
| Service | Level Gauge - Upper | Level Gauge - Lower |
| Rating | 300# | 300# |

2.18.2 Instrumentation

- LG-0001: Level Gauge (Sight Glass type) - Provides local visual indication of liquid level from LLLL (300mm) to HHLL (1300mm)

2.18.3 Component Configuration

N18A Connection Path (Upper):

- Nozzle N18A (2")

- HV0024-N18A-SOL: 2-inch Solenoid Valve

N18B Connection Path (Lower):

- Nozzle N18B (2")

- HV0025-N18B-SOL: 2-inch Solenoid Valve

Level Gauge Assembly:

- HV0026-LG-TOP: 1-inch Gate Valve - Top of gauge isolation

- LG-0001: Level Gauge (vertical orientation between upper and lower connections)

- HV0027-LG-BTM: 1-inch Gate Valve - Bottom of gauge isolation

Instrumentation Line:

- Line Number: 1"-PP01-512-PK0076-B03F9-PP

2.18.4 Header Connection

Piping Specification Change: A 1-inch gate valve separates specification B03F9 from B01M8.

This assembly connects to the Bottom Common Header line 1"-PP01-512-PK0054-B01M8-PP, joining with the N7 and N10 level transmitter assemblies.

SECTION 3: INTERCONNECTED INSTRUMENTATION HEADER SYSTEMS

3.1 Bottom Common Header Network (Liquid Level Instruments)

This header network collects connections from the lower level instruments (N7/LIT-0001, N10/LIT-0003, and N18/LG-0001) and provides common drainage to the liquid outlet system.

3.1.1 Header Line Identification

Main Header Line: 1"-PP01-512-PK0054-B01M8-PP

3.1.2 Connected Instrument Bridles

| Bridle | Nozzles | Instrument | Branch Line Number |
| --- | --- | --- | --- |
| N18 Assembly | N18A, N18B | LG-0001 | 1"-PP01-512-PK0076-B03F9-PP |
| N7 Assembly | N7A, N7B | LIT-0001 | 1"-PP01-512-PK0077-B03F9-PP |
| N10 Assembly | N10A, N10B | LIT-0003 | 1"-PP01-512-PK0078-B03F9-PP |

3.1.3 Header Correlation

The Bottom Common Header correlates with the N3 liquid outlet piping network, specifically connecting near the 4-inch line 4"-PP01-512-PK0006-B01M8-PP. This allows the level instruments to be filled/calibrated and drained through the common liquid handling system.

3.2 Top Common Header Network (Interface Level Instruments)

This header network collects connections from the upper interface level instruments (N6/LZT-0002C, N11/LZT-0002B, and N12/LZT-0002A) and provides common drainage.

3.2.1 Header Line Identification

Main Header Line: 1"-PP01-512-PK0079-B03F9-PP

3.2.2 Connected Instrument Bridles

| Bridle | Nozzles | Instrument | Branch Line Number |
| --- | --- | --- | --- |
| N12 Assembly | N12A, N12B | LZT-0002A | (Direct to header) |
| N11 Assembly | N11A, N11B | LZT-0002B | 1"-PP01-512-PK0080-B03F9-PP |
| N6 Assembly | N6A, N6B | LZT-0002C | 1"-PP01-512-PK0081-B03F9-PP |

3.2.3 Common Header Valves

- HV0052-TOP-HDR-ISO: 1-inch Gate Valve - Main header isolation

- HV0056-TOP-HDR-DRAIN: 1-inch Drain Valve - Common drain for upper instrument cluster

3.2.4 Header Connection Point

The individual lines from N6, N11, and N12 feed into this header line before the drain valve HV0056-TOP-HDR-DRAIN. The header then connects to the Bottom Common Header at a 1-inch ball valve tie-in point.

SECTION 4: COMPLETE PIPING LINE LIST

4.1 Process Lines

| Line Number | Size | From | To | Material Spec | Service | Special Requirements |
| --- | --- | --- | --- | --- | --- | --- |
| 16"-PP01-361-GF0014-B03F9-PP | 16" | DS-1 Scrapper (PID-0005-001) | Vessel N5 | B03F9-PP | Fuel Gas Inlet | NO POCKETS (NOTE-10) |
| 16"-PP01-361-GF0031-B03F9-PP | 16" | DS-3 Scrapper (PID-0007-001) | Vessel N4 | B03F9-PP | Fuel Gas Inlet | NO POCKETS (NOTE-10) |
| 14"-PP01-362-GF0001-B01E9-PP | 14" | Vessel N1 | PSV-001 Header | B01E9-PP | PSV Relief | - |
| 14"-PP01-362-GF0004-B01E9-PP | 14" | PSV Header Junction | PSV-002 | B01E9-PP | PSV Relief | - |
| 16"-PP01-362-GF0002-B01E9-PP | 16" | Vessel N2 | Fuel Gas Treatment (PID-0009-001) | B01E9-PP | Main Gas Outlet | - |
| 6"-PP01-362-GF0009-B01E9-PP | 6" | N2 Header Branch | HP Flare via BDV-0001 | B01E9-PP | Blowdown | Spec changes to B01B8 |
| 8"-PP01-362-GF0003-B01E9-PP | 8" | N2 Header Branch | HP Flare via PV-0002 | B01E9-PP | Pressure Control | Spec changes to B01B8 |
| 4"-PP01-512-PK0005-C01N9-PP | 4" | Vessel N3 | EZV-0001 | C01N9-PP | Liquid Outlet | - |
| 4"-PP01-512-PK0006-B01M8-PP | 4" | LV-0001 | Condensate Storage (PID-0024-001) | B01M8-PP | Liquid Outlet | TWO PHASE (NOTE-10) |
| 2"-PP01-567-GF0002-B03F9 | 2" | Vessel N9 | UC | B03F9 | Manual Drain | - |
| 16"-PP01-500-VK0066-B01B8 | 16" | PSV-001 Outlet | HP Flare (PID-0021-001) | B01B8 | Relief | NO POCKETS |
| 16"-PP01-500-VK0008-B01B8 | 16" | PSV-002 Outlet | HP Flare (PID-0021-001) | B01B8 | Relief | NO POCKETS |
| 8"-PP01-500-VK0026-B01B8 | 8" | Blowdown Line | HP Flare (PID-0021-001) | B01B8 | Blowdown | - |
| 10"-PP01-500-VK0010-B01B8 | 10" | PV-0002 Outlet | HP Flare (PID-0021-001) | B01B8 | Pressure Control | - |

4.2 Instrumentation Lines

| Line Number | Size | From | To | Material Spec | Service |
| --- | --- | --- | --- | --- | --- |
| 1"-PP01-512-PK0054-B01M8-PP | 1" | Common Header | N3 System | B01M8-PP | Bottom Level Instruments |
| 1"-PP01-512-PK0076-B03F9-PP | 1" | N18 Assembly | Header | B03F9-PP | LG-0001 |
| 1"-PP01-512-PK0077-B03F9-PP | 1" | N7 Assembly | Header | B03F9-PP | LIT-0001 |
| 1"-PP01-512-PK0078-B03F9-PP | 1" | N10 Assembly | Header | B03F9-PP | LIT-0003 |
| 1"-PP01-512-PK0079-B03F9-PP | 1" | Common Header | Top Instruments | B03F9-PP | Top Level Instruments |
| 1"-PP01-512-PK0080-B03F9-PP | 1" | N11 Assembly | Header | B03F9-PP | LZT-0002B |
| 1"-PP01-512-PK0081-B03F9-PP | 1" | N6 Assembly | Header | B03F9-PP | LZT-0002C |

SECTION 5: COMPLETE VALVE LIST WITH RESOLVED TAGS

5.1 Ball Valves

| Tag | Size | Location | Service | Normal Position | Notes |
| --- | --- | --- | --- | --- | --- |
| HV0003-N17-VENT | 3" | Nozzle N17 | Vent/Service | Closed | Terminates at valve |
| HV0004-PSV1-INLET | 14" | PSV-001 Inlet | PSV Isolation | LO (Locked Open) | - |
| HV0004-LV-BYPASS | 1.5" | N3 Bypass Line | Level Control Bypass | Variable | - |
| HV0006-PSV2-INLET | 14" | PSV-002 Inlet | PSV Isolation | LO (Locked Open) | - |
| HV0016-PV-INLET | 8" | PV-0002 Upstream | Pressure Control | Open | - |
| HV0018-PV-BYPASS-IN | 4" | PV-0002 Bypass | Manual Bypass | Closed | - |
| HV0021-PV-OUTLET | 10" | PV-0002 Downstream | Pressure Control | Open | - |
| HV0029-BLOWDOWN-OUTLET | 8" | BDV-0001 Downstream | Blowdown | Closed | - |
| HV0039-PSV1-OUTLET | 16" | PSV-001 Outlet | PSV Isolation | Open | - |
| HV0041-PSV2-OUTLET | 16" | PSV-002 Outlet | PSV Isolation | Open | - |
| HV0061-BLOWDOWN | 6" | Blowdown Branch | Blowdown | Closed | - |
| HV0094-N5-INLET | 16" | DS-1 Inlet Line | Inlet Isolation | Open | - |
| HV0203-N4-INLET | 16" | DS-3 Inlet Line | Inlet Isolation | Open | - |

5.2 Gate Valves

| Tag | Size | Location | Service | Normal Position | Notes |
| --- | --- | --- | --- | --- | --- |
| HV0002-N9-ISO | 2" | Nozzle N9 | Manual Drain | NC (Normally Closed) | - |
| HV0026-LG-TOP | 1" | LG-0001 Top | Level Gauge | Open | - |
| HV0027-N3-INLET-ISO | 4" | N3 Outlet | Liquid Isolation | Open | Main path upstream |
| HV0027-LG-BTM | 1" | LG-0001 Bottom | Level Gauge | Open | - |
| HV0028-N3-OUTLET-ISO | 4" | N3 Outlet | Liquid Isolation | Open | After EZV-0001 |
| HV0029-N7-GATE | 1" | N7 Assembly | Level Transmitter | Open | - |
| HV0029-LV-INLET | 1.5" | N3 Bypass | LV-0001 Inlet | Open | - |
| HV0030-LV-OUTLET | 1.5" | N3 Bypass | LV-0001 Outlet | Open | - |
| HV0032-LV-BYPASS-IN | 2" | LV-0001 Bypass | Level Control | Variable | - |
| HV0033-N10-GATE | 1" | N10 Assembly | Level Transmitter | Open | - |
| HV0041-N12-GATE | 1" | N12 Assembly | Level Transmitter | Open | - |
| HV0043-N11-GATE | 1" | N11 Assembly | Level Transmitter | Open | - |
| HV0044-N6-GATE-UP | 1" | N6 Assembly | Level Transmitter | Open | - |
| HV0045-N6-GATE-DN | 1" | N6 Assembly | Level Transmitter | Open | - |
| HV0049-N7-GATE-2 | 1" | N7 Assembly | Level Transmitter | Open | - |
| HV0050-N7-GATE-3 | 1" | N7 Assembly | Level Transmitter | Open | - |
| HV0051-N10-GATE | 1" | N10 Assembly | Level Transmitter | Open | - |
| HV0052-TOP-HDR-ISO | 1" | Top Header | Header Isolation | Open | - |
| HV0064-N8-SERVICE | 3" | Nozzle N8 | Maintenance | Closed | - |
| HV0065-N3-DRAIN | 2" | N3 Outlet | Drain | NC | - |

5.3 Globe Valves

| Tag | Size | Location | Service | Notes |
| --- | --- | --- | --- | --- |
| HV0019-PV-BYPASS-OUT | 4" | PV-0002 Bypass | Throttling | Manual bypass |

5.4 Drain Valves

| Tag | Size | Location | Service |
| --- | --- | --- | --- |
| HV0003-N10-DRAIN | 1" | N10 Assembly | Instrument Drain |
| HV0005-PSV1-DRAIN | 1" | PSV-001 Inlet | Drain |
| HV0007-PSV2-DRAIN | 1" | PSV-002 Inlet | Drain |
| HV0017-PV-DRAIN-UP | 1" | PV-0002 Upstream | Drain |
| HV0020-PV-DRAIN-DN | 1" | PV-0002 Downstream | Drain |
| HV0028-N7-DRAIN | 1" | N7 Assembly | Instrument Drain |
| HV0030-LV-DRAIN | 0.5" | LV-0001 Area | Drain |
| HV0038-PSV1-OUTLET-DRAIN | 1" | PSV-001 Outlet | Drain |
| HV0040-N12-DRAIN | 1" | N12 Assembly | Instrument Drain |
| HV0040-PSV2-OUTLET-DRAIN | 1" | PSV-002 Outlet | Drain |
| HV0042-N11-DRAIN | 1" | N11 Assembly | Instrument Drain |
| HV0051-N9-DRAIN | 1" | N9 Manual Drain | Drain |
| HV0056-TOP-HDR-DRAIN | 1" | Top Header | Common Drain |

5.5 Solenoid Valves (2-inch)

| Tag | Location | Instrument Served |
| --- | --- | --- |
| HV0011-N13-SOL | Nozzle N13 | PZT-0001A |
| HV0012-N14-SOL | Nozzle N14 | PZT-0001B |
| HV0013-N15-SOL | Nozzle N15 | PZT-0001C |
| HV0014-N16-SOL | Nozzle N16 | PIT-0002 |
| HV0022-N7A-SOL | Nozzle N7A | LIT-0001 |
| HV0023-N7B-SOL | Nozzle N7B | LIT-0001 |
| HV0024-N18A-SOL | Nozzle N18A | LG-0001 |
| HV0025-N18B-SOL | Nozzle N18B | LG-0001 |
| HV0030-N10A-SOL | Nozzle N10A | LIT-0003 |
| HV0031-N10B-SOL | Nozzle N10B | LIT-0003 |
| HV0034-N6A-SOL | Nozzle N6A | LZT-0002C |
| HV0035-N6B-SOL | Nozzle N6B | LZT-0002C |
| HV0036-N11A-SOL | Nozzle N11A | LZT-0002B |
| HV0037-N11B-SOL | Nozzle N11B | LZT-0002B |
| HV0038-N12A-SOL | Nozzle N12A | LZT-0002A |
| HV0039-N12B-SOL | Nozzle N12B | LZT-0002A |

5.6 Check Valves

| Tag | Size | Location | Service |
| --- | --- | --- | --- |
| CV-N4-INLET | 16" | DS-3 Inlet Line | Backflow Prevention |
| CV-N5-INLET | 16" | DS-1 Inlet Line | Backflow Prevention |
| HV0001-N9-CHECK | 2" | N9 Drain Line | Backflow Prevention |

5.7 Control Valves

| Tag | Size | Service | Controller | Fail Position |
| --- | --- | --- | --- | --- |
| PV-0002 | 8" | Pressure Control | PIC-0002 | - |
| LV-0001 | 1.5" | Level Control | LIC-0001 | FC |
| BDV-0001 | 6" | Blowdown Control | - | - |
| EZV-0001 | 4" | Emergency Shutdown | SIS | FC |

SECTION 6: COMPLETE INSTRUMENTATION LIST

6.1 Pressure Instruments

| Tag | Type | Location | Function | Voting Logic |
| --- | --- | --- | --- | --- |
| PI-0001A | Pressure Indicator | N13 | Local Indication, HH Alarm | - |
| PI-0001B | Pressure Indicator | N14 | Local Indication, HH Alarm | - |
| PI-0001C | Pressure Indicator | N15 | Local Indication, HH Alarm | - |
| PZT-0001A | Pressure Transmitter | N13 | Safety System | 2oo3 (362-004) |
| PZT-0001B | Pressure Transmitter | N14 | Safety System | 2oo3 (362-004) |
| PZT-0001C | Pressure Transmitter | N15 | Safety System | 2oo3 (362-004) |
| PIT-0002 | Pressure Transmitter | N16 | Process Control | - |
| PIC-0002 | Pressure Controller | N16 | Controls PV-0002 | - |
| PG-0001 | Pressure Gauge | N2 Header | Local Indication | - |

6.2 Level Instruments

| Tag | Type | Location (Nozzles) | Function | Voting Logic |
| --- | --- | --- | --- | --- |
| LG-0001 | Level Gauge | N18A/N18B | Local Visual Indication | - |
| LIT-0001 | Level Transmitter | N7A/N7B | Process Control | - |
| LIT-0003 | Level Transmitter | N10A/N10B | Process Indication | - |
| LIC-0001 | Level Controller | - | Controls LV-0001 | - |
| LZT-0002A | Level Transmitter (GWR) | N12A/N12B | Safety System | 2oo3 (362-003/007) |
| LZT-0002B | Level Transmitter (GWR) | N11A/N11B | Safety System | 2oo3 (362-003/007) |
| LZT-0002C | Level Transmitter (GWR) | N6A/N6B | Safety System | 2oo3 (362-003/007) |
| LI-0002A | Level Indicator | Associated with LZT-0002A | Local Indication | - |
| LI-0002B | Level Indicator | Associated with LZT-0002B | Local Indication | - |
| LI-0002C | Level Indicator | Associated with LZT-0002C | Local Indication | - |
| LV-0002A | Level Valve | Associated with LZT-0002A | - | - |
| LV-0002B | Level Valve | Associated with LZT-0002B | - | - |
| LV-0002C | Level Valve | Associated with LZT-0002C | - | - |

6.3 Corrosion Instruments

| Tag | Type | Location | Function |
| --- | --- | --- | --- |
| CI-0001 | Corrosion Indicator | N3 Outlet Branch | Local Indication |
| CIT-0001 | Corrosion Transmitter | N3 Outlet Branch | Remote Monitoring |

6.4 Safety Relief Devices

| Tag | Type | Set Pressure | Relief Case | Size |
| --- | --- | --- | --- | --- |
| PSV-001 | Pressure Safety Valve | 14.0 barg | DS-3 PCV Failure | 8T10 |
| PSV-002 | Pressure Safety Valve | 14.0 barg | DS-3 PCV Failure | 8T10 |

SECTION 7: CONTROL LOOP DESCRIPTIONS

7.1 Pressure Control Loop (PIC-0002 → PV-0002)

Purpose: Maintains vessel operating pressure within 9.0-10.4 barg range by modulating gas flow to HP Flare.

Loop Components:

- PIT-0002: Pressure transmitter at Nozzle N16 senses vessel pressure

- PIC-0002: Controller compares measured pressure to setpoint

- PV-0002: 8-inch control valve on line 8"-PP01-362-GF0003-B01E9-PP modulates gas flow

Control Action:

- Increasing vessel pressure → PIC-0002 output increases → PV-0002 opens → More gas flows to flare → Pressure decreases

- Decreasing vessel pressure → PIC-0002 output decreases → PV-0002 closes → Less gas flows to flare → Pressure increases

7.2 Level Control Loop (LIC-0001 → LV-0001)

Purpose: Maintains vessel liquid level at Normal Liquid Level (800mm) by modulating liquid discharge.

Loop Components:

- LIT-0001: Level transmitter at Nozzles N7A/N7B senses liquid level

- LIC-0001: Controller compares measured level to NLL setpoint (800mm)

- LV-0001: 1.5-inch control valve on N3 outlet bypass modulates liquid flow

Control Action:

- Rising level → LIC-0001 output increases → LV-0001 opens → More liquid drains → Level decreases

- Falling level → LIC-0001 output decreases → LV-0001 closes → Less liquid drains → Level increases

7.3 High Pressure Safety Instrumented Function (PZT → 2oo3 → ESD)

Purpose: Provides independent high-pressure protection to prevent vessel overpressure.

Loop Components:

- PZT-0001A, PZT-0001B, PZT-0001C: Three independent pressure transmitters

- 2oo3 Voting Logic (362-004): Requires 2 of 3 transmitters to confirm high pressure

- ESD System: Initiates protective actions

Safety Action: When 2 out of 3 transmitters detect pressure above the high-pressure trip setpoint, the voting logic sends a trip signal to the ESD system, which closes EZV-0001 and initiates other protective actions.

7.4 Level Safety Instrumented Function (LZT → 2oo3 → ESD)

Purpose: Provides independent level protection for both high-high and low-low level conditions.

Loop Components:

- LZT-0002A, LZT-0002B, LZT-0002C: Three independent GWR level transmitters

- 2oo3 Voting Logic (362-003 for HHLL, 362-007 for LLLL): Requires 2 of 3 transmitters to confirm level alarm

- ESD System: Initiates protective actions

Safety Actions:

- HHLL (1300mm): Voting logic 362-003 trips to prevent liquid carryover to downstream equipment

- LLLL (300mm): Voting logic 362-007 trips to prevent pump cavitation or loss of seal

SECTION 8: REFERENCE DRAWINGS

| Drawing Number | Title | Connection Point |
| --- | --- | --- |
| N-PG-PP01-PR-PID-0005-001 | DS-1 Scrapper Receiver | Inlet via N5 |
| N-PG-PP01-PR-PID-0007-001 | DS-3 Scrapper Receiver | Inlet via N4 |
| N-PG-PP01-PR-PID-0009-001 | Fuel Gas Treatment Package | Gas Outlet via N2 |
| N-PG-PP01-PR-PID-0021-001 | HP Flare Header | PSV Outlets, Blowdown, Pressure Control |
| N-PG-PP01-PR-PID-0024-001 | Condensate Storage Vessel | Liquid Outlet via N3 |

SECTION 9: NOTES REFERENCE

| Note | Description | Application |
| --- | --- | --- |
| NOTE-2 | Inlet nozzle connection requirements | N4, N5 inlet nozzles |
| NOTE-7 | Design temperature requirements | Vessel design -20°C to 100°C |
| NOTE-10 | NO POCKETS requirement, TWO PHASE designation | Inlet lines, N3 outlet line |

SECTION 10: RESOLVED TAG DUPLICATIONS SUMMARY

The following table provides a complete cross-reference of all valve tags that appeared duplicated in the source documentation, now resolved with unique descriptive suffixes:

| Original Duplicated Tag | Resolved Tag 1 | Location 1 | Resolved Tag 2 | Location 2 | Resolved Tag 3 (if applicable) | Location 3 |
| --- | --- | --- | --- | --- | --- | --- |
| HV0004 | HV0004-PSV1-INLET | PSV-001 inlet (14" Ball) | HV0004-LV-BYPASS | N3 bypass (1.5" Ball) | - | - |
| HV0027 | HV0027-N3-INLET-ISO | N3 outlet (4" Gate) | HV0027-LG-BTM | LG-0001 bottom (1" Gate) | - | - |
| HV0028 | HV0028-N3-OUTLET-ISO | N3 outlet (4" Gate) | HV0028-N7-DRAIN | N7 drain (1" Drain) | - | - |
| HV0029 | HV0029-BLOWDOWN-OUTLET | BDV downstream (8" Ball) | HV0029-N7-GATE | N7 assembly (1" Gate) | HV0029-LV-INLET | N3 bypass (1.5" valve) |
| HV0030 | HV0030-N10A-SOL | N10A solenoid (2") | HV0030-LV-OUTLET | N3 bypass (1.5" valve) | HV0030-LV-DRAIN | N3 bypass (0.5" drain) |
| HV0038 | HV0038-PSV1-OUTLET-DRAIN | PSV-001 drain (1") | HV0038-N12A-SOL | N12A solenoid (2") | - | - |
| HV0039 | HV0039-PSV1-OUTLET | PSV-001 outlet (16" Ball) | HV0039-N12B-SOL | N12B solenoid (2") | - | - |
| HV0040 | HV0040-PSV2-OUTLET-DRAIN | PSV-002 drain (1") | HV0040-N12-DRAIN | N12 assembly (1" Drain) | - | - |
| HV0041 | HV0041-PSV2-OUTLET | PSV-002 outlet (16" Ball) | HV0041-N12-GATE | N12 assembly (1" Gate) | - | - |
| HV0051 | HV0051-N9-DRAIN | N9 drain (1") | HV0051-N10-GATE | N10 assembly (1" Gate) | - | - |

SECTION 11: COMPLETE NOZZLE SUMMARY TABLE

| Nozzle | Size | Service | Primary Equipment | Key Valves (Resolved Tags) | Line Number |
| --- | --- | --- | --- | --- | --- |
| N1 | 14" | PSV Relief Header | PSV-001, PSV-002 | HV0004-PSV1-INLET, HV0006-PSV2-INLET | 14"-PP01-362-GF0001-B01E9-PP |
| N2 | 16" | Gas Outlet | PV-0002, BDV-0001 | HV0015-N2-PG, HV0016-PV-INLET, HV0061-BLOWDOWN | 16"-PP01-362-GF0002-B01E9-PP |
| N3 | 4" | Liquid Outlet | EZV-0001, LV-0001 | HV0027-N3-INLET-ISO, HV0028-N3-OUTLET-ISO, HV0065-N3-DRAIN | 4"-PP01-512-PK0005-C01N9-PP |
| N4 | 12" | Gas Inlet (DS-3) | - | HV0203-N4-INLET, CV-N4-INLET | 16"-PP01-361-GF0031-B03F9-PP |
| N5 | 12" | Gas Inlet (DS-1) | - | HV0094-N5-INLET, CV-N5-INLET | 16"-PP01-361-GF0014-B03F9-PP |
| N6A/N6B | 2" | Level Bridle | LZT-0002C | HV0034-N6A-SOL, HV0035-N6B-SOL, HV0044-N6-GATE-UP, HV0045-N6-GATE-DN | 1"-PP01-512-PK0081-B03F9-PP |
| N7A/N7B | 2" | Level Bridle | LIT-0001 | HV0022-N7A-SOL, HV0023-N7B-SOL, HV0029-N7-GATE | 1"-PP01-512-PK0077-B03F9-PP |
| N8 | 3" | Maintenance | - | HV0064-N8-SERVICE | - |
| N9 | 2" | Manual Drain | UC | HV0002-N9-ISO, HV0001-N9-CHECK, HV0051-N9-DRAIN | 2"-PP01-567-GF0002-B03F9 |
| N10A/N10B | 2" | Level Bridle | LIT-0003 | HV0030-N10A-SOL, HV0031-N10B-SOL, HV0033-N10-GATE | 1"-PP01-512-PK0078-B03F9-PP |
| N11A/N11B | 2" | Level Bridle | LZT-0002B | HV0036-N11A-SOL, HV0037-N11B-SOL, HV0042-N11-DRAIN, HV0043-N11-GATE | 1"-PP01-512-PK0080-B03F9-PP |
| N12A/N12B | 2" | Level Bridle | LZT-0002A | HV0038-N12A-SOL, HV0039-N12B-SOL, HV0040-N12-DRAIN, HV0041-N12-GATE | - |
| N13 | 2" | Pressure Instr. | PZT-0001A, PI-0001A | HV0011-N13-SOL | - |
| N14 | 2" | Pressure Instr. | PZT-0001B, PI-0001B | HV0012-N14-SOL | - |
| N15 | 2" | Pressure Instr. | PZT-0001C, PI-0001C | HV0013-N15-SOL | - |
| N16 | 2" | Pressure Control | PIT-0002, PIC-0002 | HV0014-N16-SOL | - |
| N17 | 3" | Vent/Service | - | HV0003-N17-VENT | Terminates |
| N18A/N18B | 2" | Level Gauge | LG-0001 | HV0024-N18A-SOL, HV0025-N18B-SOL, HV0026-LG-TOP, HV0027-LG-BTM | 1"-PP01-512-PK0076-B03F9-PP |

SECTION 12: REMAINING UNCERTAINTIES REQUIRING FIELD VERIFICATION

Despite resolution of tag duplications, the following items still require field verification:

| Item | Issue | Recommended Action |
| --- | --- | --- |
| Vessel OD | Source states "OD 5500" which conflicts with ID 2200mm and Length 5500mm | Confirm vessel dimensions from nameplate |
| Design Temperature | One source says "-23°C to 72°C", another says "-20°C to 100°C" | Verify from vessel nameplate |
| LV-0002A/B/C | Associated with LZT transmitters but exact location/function unclear | Field verify installation and control function |
| Nozzle N14 vs HV0003 | Source originally conflicted on N14 being pressure transmitter vs 3" ball valve | Confirm N14 is PZT-0001B connection as documented |
| PV-0002 Line Number | Two different line numbers cited in source documentation | Verify correct line number is 8"-PP01-362-GF0003-B01E9-PP |